## Master Survey 38 ULBs
Appendix A: Details of Greenfield Stretches Surveyed at 38 ULBs from Different Clusters
Sl. | District | Cluster | ULB Name | ULB Category (Municipality / NAC/ Corporation) | Ward No | Road Details | [6 empty] | Road Group Categories - Based on Traffic Specific Details |  |  |  |  | Pole Parameters |  |  |  | Prospective nearest Location on Road for ULB transformer / Switching Point identified by ULB in Consultation with Distribution Utility | Other Remarks if Any | Number of Poles | Number of Outrach Arms | Number of LED Luminaires of Different ratings (W) |  |  |  | kW Load Estimate for Given Stretch (kW) | Feeder Panel Requirement Details for Given Road Streatchs |  |  | Length of 'UNARMOURED PVC SHEATHED CABLES - 1.1 KV TWIN CORE, ALUMINIUM CONDUCTOR, PVC INSULATED, INNER SHEATHED CONFORMING TO IS : 1554 (PART I)' |  |  |  | Earting of Poles and Feeder Panels
[6 empty] | Name of Road | Road Width (meter) | Location Start Point |  | Location End Point |  | Road Length to be Covered for New Street Lighting (meter) | Traffic Flow | A1 Rapid and Dense Motor Vehicle Traffic | A2 Considerable volume of mixed traffic | B1 Local traffic routes, shopping streets | B2 /C Residential Area Roads | Proposed Pole Arrangements | Proposed Pole Span (meter) | Proposed Pole Height | Pole Special Requirement | [16 empty] | Earthing Electrode (One for every 5th Pole) | GI Strip of 25 mm X 5 mm to Earth all poles
[8 empty] | Name | GPS Co-ordinates | Name | GPS Co-ordinates | [14 empty] | 120 | 90 | 70 | 45 |  | Number of Panels | kW Load Per Feeder Panel | Kw Rating of Feeder Panel | 2.5 Sq mm | 6 Sq mm | 10 Sq mm | 25 Sq mm
1 | Jagatsinghpur | A | Paradeep | Municipality | 17 | Marin drive road | 16 | Balijatra Padia | 20.254488,86.654731 | SandhaKuda Entrance | 20.253283,86.651788 | 300 | 2W |  | Y |  |  | DS | 27 | 9 |  | Existing street light pole | Middle pole arrangement not recommended - Site specific reason | 22 | 22 | 0 | 22 | 0 | 0 | 1.98 | 1 | 1.98 | 3 | 660 | 0 | 0 | 0 | 4 | 660
2 | Jagatsinghpur | A | Paradeep | Municipality | 18 | SandhaKuda village road | 3.5 | Start Point | 20.251964,86.647858 | End point | 20.252747,86.648373 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | EXSISTING UTILITY TRANSFORMER |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
3 | Jagatsinghpur | A | Paradeep | Municipality | 18 | SandhaKuda Marin drive | 8 | Sandhakuda Church | 20.251760,86.647004 | End point | 20.247381,86.633927 | 1500 | 2W |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 56 | 56 | 0 | 56 | 0 | 0 | 5.04 | 1 | 5.04 | 7.5 | 0 | 0 | 1650 | 0 | 11 | 1650
4 | Jagatsinghpur | A | Paradeep | Municipality | 16 | Marin drive road | 16 | Balijatra Padia | 20.255994,86.658650 | Hanuman Temple | 20.259896,86.667045 | 1000 | 2W |  |  | Y |  | DS | 27 | 9 |  | Existing street light pole | Middle pole arrangement not recommended site specific reason | 74 | 74 | 0 | 0 | 74 | 0 | 5.18 | 1 | 5.18 | 7.5 | 0 | 0 | 2200 | 0 | 15 | 2200
5 | Jagatsinghpur | A | Paradeep | Municipality | 16 | Marin drive road | 6 | Marin drive | 20.257585,86.661850 | Nuabazar Market Sq.. | 20.260246,86.660736 | 300 | 2W |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE BOTH SIDE |  | 15 | 15 | 0 | 0 | 15 | 0 | 1.05 | 1 | 1.05 | 3 | 330 | 0 | 0 | 0 | 3 | 330
6 | Jagatsinghpur | A | Paradeep | Municipality | 13 | Bangalipada Road | 6 | Part of Jagannath Mandir | 20.261036,86.642329 | Smasan Ghat | 20.256495,86.633345 | 1400 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING PPT STREET LIGHT POLE |  | 70 | 70 | 0 | 0 | 70 | 0 | 4.9 | 1 | 4.9 | 7.5 | 0 | 0 | 1540 | 0 | 14 | 1540
7 | Jagatsinghpur | A | Paradeep | Municipality | 13 | Dump yard road | 6 | Dom yard road | 20.258431,86.636993 | Bhimabhoi Colony | 20.262143,86.636987 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
8 | Jagatsinghpur | A | Paradeep | Municipality | 13 | Bangalipada village Road | 3 | Village start | 20.259055,86.642801 | Village end | 20.258493,86.639710 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
9 | Jagatsinghpur | A | Paradeep | Municipality | 13 | L I C Colony Road | 3.5-5 | L I C Colony Road | 20.265637,86.643318 | Mundapada basti road | 20.265727,86.643483 + 20.267011,86.644686 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT FEEDER |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
10 | Jagatsinghpur | A | Paradeep | Municipality | 1 | Nehru Bangla Basti Multiple Basti road L-1 | 2.5 | Basti Area 1 | 20.286186,86.710053 |  | 20.289025,86.713446 | 480 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 24 | 24 | 0 | 0 | 0 | 24 | 1.08 | 1 | 1.08 | 3 | 528 | 0 | 0 | 0 | 5 | 528
14 | Jagatsinghpur | A | Paradeep | Municipality | 1 | Nehru Bangla Basti Multiple Basti road L3 | 2.5 | Basti Area 2 | 20.286650,86.710695 |  | 20.287179,86.712149 | 550 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 605 | 0 | 0 | 0 | 6 | 605
16 | Jagatsinghpur | A | Paradeep | Municipality | 1 | Nehru Bangla Basti Multiple Basti road L5 | 2.5 | Basti Area 3 | 20.287980,86.713203 |  | 20.286212,86.711112 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
19 | Jagatsinghpur | A | Paradeep | Municipality | 1 | Fisher Colony | 4 | Start Point | 20.284333,86.707399 | End point | 20.283751,86.706500 | 100 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 5 | 5 | 0 | 0 | 0 | 5 | 0.225 | 1 | 0.225 | 3 | 110 | 0 | 0 | 0 | 1 | 110
20 | Jagatsinghpur | A | Paradeep | Municipality | 2 | Bali plot Entrance road | 4.5 | Atharbanki Starting point | 20.289537,86.655245 | Bali Plot Ending | 20.291001,86.655767 | 150 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 8 | 8 | 0 | 0 | 8 | 0 | 0.56 | 1 | 0.56 | 3 | 165 | 0 | 0 | 0 | 2 | 165
21 | Jagatsinghpur | A | Paradeep | Municipality | 2 | Ambika School to Santoshi Temple | 3.5 | Ambika School | 20.288766,86.650915 | Santoshi Temple | 20.287372,86.650859 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
22 | Jagatsinghpur | A | Paradeep | Municipality | 5 | PPL Road | 8 | PPL Main Gate | 20.305594,86.636760 | PPL Label Crossing | 20.281390,86.617557 | 3600 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 133 | 133 | 0 | 133 | 0 | 0 | 11.97 | 2 | 5.985 | 7.5 | 0 | 0 | 3960 | 0 | 27 | 3960
23 | Jagatsinghpur | A | Paradeep | Municipality | 5 | Santoshi Nagar Village road | 3.5 | PPL Road | 20.297593,86.630681 | Santoahi Nagar | 20.296720,86.631440 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
24 | Jagatsinghpur | A | Paradeep | Municipality | 3 | IFFCO Chhack Under Cover Belt | 5 | IFFCO Chhack | 20.304150,86.641579 | End Point | 20.294035,86.660231 | 3000 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 150 | 150 | 0 | 0 | 0 | 150 | 6.75 | 2 | 3.375 | 5 | 0 | 3300 | 0 | 0 | 30 | 3300
1 | Jajpur | C | Vyasanagar | Municipality | 26 | Mundamala Adibashi sahi | 6 | Adibashi Sahi | 20.928825,86.102670 | Khadahata Salachhaka | 20.920758,86.119764 | 900 | M |  |  | Y |  | SS | 27 | 9 |  | EXISTING TRANSFORMER BEFORE 100M |  | 33 | 33 | 0 | 0 | 33 | 0 | 2.31 | 1 | 2.31 | 3 | 990 | 0 | 0 | 0 | 7 | 990
2 | Jajpur | C | Vyasanagar | Municipality | 23 | KOPONDO | 3 | MHARANA SAHI | 20.933205,86.131150 | INFRONT OF SENAPATI HOUSE | 20.931714,86.130873 | 180 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 9 | 9 | 0 | 0 | 0 | 9 | 0.405 | 1 | 0.405 | 3 | 198 | 0 | 0 | 0 | 2 | 198
3 | Jajpur | C | Vyasanagar | Municipality | 26 | RAGHUJI TO SARBARA ROAD | 4.5 | PANI TANKI | 20.930810,86.118425 | ASHRAM | 20.937460,86.115433 | 1100 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING TRANSFORMER FROM STARTING POLE AT 600M |  | 55 | 55 | 0 | 0 | 0 | 55 | 2.475 | 1 | 2.475 | 5 | 0 | 1210 | 0 | 0 | 11 | 1210
4 | Jajpur | C | Vyasanagar | Municipality | 24 | ASHRAM ROAD | 4.5 | CHUNABHATI SCHOOL | 20.938561,86.120170 | PLOT CHHACK | 20.939297,86.123213 | 330 | M |  |  |  | Y | SS | 20 | 8 |  | NEW TRANSFORMER TO BE INSTALED NEAR ASHRAM |  | 17 | 17 | 0 | 0 | 0 | 17 | 0.765 | 1 | 0.765 | 3 | 363 | 0 | 0 | 0 | 3 | 363
5 | Jajpur | C | Vyasanagar | Municipality | 20 | AP ABDUL KALAM ROAD | 3 | STARTING POINT | 20.946012,86.140418 | END POINT | 20.946635,86.142017 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING TRANSFORMER |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
6 | Jajpur | C | Vyasanagar | Municipality | 12 | PANI TANKI HINGULAI ROAD | 6 | PANINTANKI | 20.955327,86.138030 | JAGSAHI COLONY | 20.961002,86.129260 | 1100 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING TRANSFORMER AT STARTING POINT |  | 55 | 55 | 0 | 0 | 55 | 0 | 3.85 | 1 | 3.85 | 5 | 0 | 1210 | 0 | 0 | 11 | 1210
7 | Jajpur | C | Vyasanagar | Municipality | 8 | FOREST ROAD | 3.3 | FOREST ROAD | 20.955693,86.117710 | VYASANAGAR | 20.956289,86.116101 | 180 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 9 | 9 | 0 | 0 | 0 | 9 | 0.405 | 1 | 0.405 | 3 | 198 | 0 | 0 | 0 | 2 | 198
8 | Jajpur | C | Vyasanagar | Municipality | 3 | XAVIOUR SCHOOL ROAD | 4 | NEAR STADIUM | 20.948706,86.116116 | LAXMI NAGAR | 20.943013,86.112485 | 380 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 19 | 19 | 0 | 0 | 19 | 0 | 1.33 | 1 | 1.33 | 3 | 418 | 0 | 0 | 0 | 4 | 418
9 | Jajpur | C | Vyasanagar | Municipality | 3 | FERROCHROME PLANT ROAD | 6 | FERROCHROM ROAD | 20.948503,86.108781 | XAVIOUR COLLAGE | 20.947453,86.105124 | 400 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 20 | 20 | 0 | 0 | 20 | 0 | 1.4 | 1 | 1.4 | 3 | 440 | 0 | 0 | 0 | 4 | 440
10 | Jajpur | C | Vyasanagar | Municipality | 1 | JODA BARA TO SAROBARA | 3 | JODA BARA | 20.938756,86.100793 | SAROBARA | 20.933761,86.110686 | 1400 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 70 | 70 | 0 | 0 | 70 | 0 | 4.9 | 1 | 4.9 | 7.5 | 0 | 0 | 1540 | 0 | 14 | 1540
11 | Jajpur | C | Vyasanagar | Municipality | 25 | SARABORA ROAD NO.2 | 4 | SARABORA ROAD | 20.936185,86.104472 | ANNATHA ASHRAM | 20.97609,86.115460 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING POLE |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
12 | Jajpur | C | Vyasanagar | Municipality | 26 | JAGANNATH MANDIRA ROAD | 3.5 | ALLEKHA MATHA | 20.933079,86.114191 | JAGANNATH MANDIRA | 20.929579,86.117329 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
1 | Kendrapara | C | Pattamundai | NAC | 2-19 | BY PASS TO SANDHA PALLI | 5 | BELATAL BYPASS BRIDGE | 20.581082,86.55120 | TARINI TEMPLE SANDHAPALLI | 20.589050,86.541465 | 1800 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREETLIGHT POLE |  | 90 | 90 | 0 | 0 | 90 | 0 | 6.3 | 1 | 6.3 | 12 | 0 | 0 | 0 | 1980 | 18 | 1980
2 | Kendrapara | C | Pattamundai | NAC | 19-2 | SUKUA BASTI | 3 | BASTI START POINT | 20.581662,86.557854 | SANDHAPALLI BRIDGE | 20.590135,86.540069 | 2100 | M |  |  |  | Y | SS | 20 | 8 |  | EXSISTING TRANSFORMER |  | 105 | 105 | 0 | 0 | 0 | 105 | 4.725 | 1 | 4.725 | 7.5 | 0 | 0 | 2310 | 0 | 21 | 2310
3 | Kendrapara | C | Pattamundai | NAC | 11-13 | SANDHA SAHI (KENAL ROAD) | 3 | MAHIMA ASHRAMA | 20.580890,86.547308 | COLLEGE BRIDGE | 20.577106,86.574144 | 850 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING TRANSFORMER |  | 43 | 43 | 0 | 0 | 0 | 43 | 1.935 | 1 | 1.935 | 3 | 935 | 0 | 0 | 0 | 9 | 935
4 | Kendrapara | C | Pattamundai | NAC | 9-15 | RAJNAGAR ROAD | 6 | PATTAMUNDAI COLLEGE BRIDGE | 20.577389,86.574474 | SUVENDU PATRA(ALABA) | 20.569826,86.588264 | 1700 | M |  | Y |  |  | SS | 27 | 9 |  | EXISTING TRANSFORMER ALABA VILLAGE |  | 63 | 63 | 0 | 63 | 0 | 0 | 5.67 | 1 | 5.67 | 7.5 | 0 | 0 | 1870 | 0 | 13 | 1870
5 | Kendrapara | C | Pattamundai | NAC | 15 | ALABA KENAL ROAD | 3 | ALABA CHHAKA | 20.567187,86.591986 | VEDISAHI BRIDGE | 20.566288,86.594108 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING TRANSFORMER ALAVA MARKET |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
6 | Kendrapara | C | Pattamundai | NAC | 15 | RAJNAGAR ROAD | 6 | VEDISAHI BRIDGE |  | ALAVA MARKET |  | 300 | M |  | Y |  |  | SS | 27 | 9 |  | DO |  | 11 | 11 | 0 | 11 | 0 | 0 | 0.99 | 1 | 0.99 | 3 | 330 | 0 | 0 | 0 | 2 | 330
7 | Kendrapara | C | Pattamundai | NAC | 15-16 | ALAVA KENAL ROAD BASTI | 3 | VASTI START | 20.566877,86.590603 | TINIMUHANI BRIDGE | 20.562595,86.580768 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
8 | Kendrapara | C | Pattamundai | NAC | 12-16 | VAKTAR BRIDGE TINIMUHANI | 6.5 | VAKTARPUR BRIDGE | 20.570968,86.59560 |  | 20.563306,86.580793 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
9 | Kendrapara | C | Pattamundai | NAC | 16 | MATIA KENAL ROAD | 3 | TINIMUHANI STARTING POINT |  | ARAVA |  | 400 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING TRANSFORMER FROM 400M |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
10 | Kendrapara | C | Pattamundai | NAC | 16 | RAJNAGAR ROAD | 6 | TINIMUHANI BRIDGE | 20.563004,86.580154 | GOVT.ITI MATIA | 20.565606,86.575971 | 550 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 20 | 20 | 0 | 20 | 0 | 0 | 1.8 | 1 | 1.8 | 3 | 605 | 0 | 0 | 0 | 4 | 605
11 | Kendrapara | C | Pattamundai | NAC | 16 | VILLAGE ROAD | 4.5 | SHIVA TEMPLE | 20.565615,86.575973 | CHAPADA SCHOOL | 20.564860,86.574876 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
12 | Kendrapara | C | Pattamundai | NAC | 17-14 | KELA SAHI- POKHORIAPADA KENAL ROAD | 3-5 | POKHORIA PADA | 20.567794,86.570014 | KELASAHI BASTI END | 20.556930,86.566220 | 1500 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 75 | 75 | 0 | 0 | 0 | 75 | 3.375 | 1 | 3.375 | 5 | 0 | 1650 | 0 | 0 | 15 | 1650
13 | Kendrapara | C | Pattamundai | NAC | 16 | VILLAGE ROAD | 4 | VASANTA SAHU HOUSE | 20.556393,86.573097 | KANDIA | 20.552594,86.564333 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
14 | Kendrapara | C | Pattamundai | NAC | 18 | TATNA ROAD DHANKIDHIA | 3.5 | JAIRAM BEHERA HOUSER | 20.570592,86.563548 | ASHOK MOHANTI HOUSE | 20.562316,86.565410 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | D0 |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
15 | Kendrapara | C | Pattamundai | NAC | 18 |  | 3-5 | DO | 20.570939,86.5628521 | MANGALA TEMPLE | 20.570072,86.561174 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
16 | Kendrapara | C | Pattamundai | NAC | 20 | JENA SAHI VILLAGE ROAD | 3.5 | MANAGOBINDA JENA | 20.568649,86.556609 | MANGALA TEMPLE | 20.567514,86.556287 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
17 | Kendrapara | C | Pattamundai | NAC | 20 | THAKURA PATANA VILLAGE ROAD | 3 | ABHAYA DAS HOUSE | 20.572982,86.552776 | BISWANATH BEHERA |  | 150 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
18 | Kendrapara | C | Pattamundai | NAC | 4 | CHADHEIDIAN VILLAGE ROAD | 3.5 | STARTING POINT | 20.591939,86.553227 | ENDING POINT | 20.592335,86.550210 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING TRANSFORMER |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
19 | Kendrapara | C | Pattamundai | NAC | 5 | ALI ROAD | 6.5 | STARTING POINT | 20.595569,86.586709 | PATRAPUR | 20.593191,86.582582 | 1000 | M |  | Y |  |  | SS | 27 | 9 |  | EXISTING LT POLE |  | 37 | 37 | 0 | 37 | 0 | 0 | 3.33 | 1 | 3.33 | 5 | 0 | 1100 | 0 | 0 | 7 | 1100
1 | Khorda | A | Banpur | NAC | 1 | ACHUTRAJPUR VILLAGE ROAD | 3.7 | BENIA POND | 19.780210,85.158985 | GODABARISHA MAHAVIDYALAYA | 185.1577949.779142, | 200 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIHGHT POINT NEAR BENIA POND |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
2 | Khorda | A | Banpur | NAC | 1 | KUMARANGA CHACK COLLEGE ROAD | 5 | HATIMUNDA | 19.779301,85.148928 | KALIA TOTA | 19.779779,85.145173 | 400 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIHGHT POLE |  | 20 | 20 | 0 | 0 | 20 | 0 | 1.4 | 1 | 1.4 | 3 | 440 | 0 | 0 | 0 | 4 | 440
3 | Khorda | A | Banpur | NAC | 12 | COURT ROAD | 4.5 | COURT ROAD MATIA POKHARI | 19.796142,85.170668 | BADASANKHA BRIDGE |  | 500 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIHGHT POLE |  | 25 | 25 | 0 | 0 | 25 | 0 | 1.75 | 1 | 1.75 | 3 | 550 | 0 | 0 | 0 | 5 | 550
4 | Khorda | A | Banpur | NAC | 13 | COURT ROAD LEAN | 2.5 | COURT SIDE | 19.792089,85.176902 | COURT SIDE | 19791818,85.176012 | 100 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIHGHT POLE |  | 5 | 5 | 0 | 0 | 0 | 5 | 0.225 | 1 | 0.225 | 3 | 110 | 0 | 0 | 0 | 1 | 110
1 | Balasore | C | Jaleswar | NAC | 1 | Rajpur village road | 3.6 | Jhadeswarpur | 21.797850,86.214692 | Ending point | 21.799057,87.219925 | 140 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 7 | 7 | 0 | 0 | 0 | 7 | 0.315 | 1 | 0.315 | 3 | 154 | 0 | 0 | 0 | 1 | 154
2 | Balasore | C | Jaleswar | NAC | 1-3 | Jhadeswarpur village road | 3 | Starting point | 21.800318,87.215437 | Sheckbal | 21.802818,87.217677 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
3 | Balasore | C | Jaleswar | NAC | 3-7 | Sheckbal village road | 2.5 | Starting point | 21.804018,87.218254 | Sasanbad | 21.807499,87.218978 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Existing lt line |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
4 | Balasore | C | Jaleswar | NAC | 7 | Sasanbad village road | 3 | Starting point | 21.809101,87.220215 | Ending point | 21.809971,87.220321 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
5 | Balasore | C | Jaleswar | NAC | 7-8 | Sasanabad reblock road | 3 | Sasanbad chhack | 21.810204,87.219611 | Pancha ghanta village road | 21.813457,87.219100 | 650 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 33 | 33 | 0 | 0 | 0 | 33 | 1.485 | 1 | 1.485 | 3 | 715 | 0 | 0 | 0 | 7 | 715
6 | Balasore | C | Jaleswar | NAC | 8-7 | pancha ghanta village road 1 | 3 | Banabihari Das house | 21.812510,87.221401 | Budhia bindhoni | 21.809439,87.222283 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
7 | Balasore | C | Jaleswar | NAC | 8-9 | pancha ghanta village road 2 | 3 | Sudhir Das house | 21.813241,87.225529 | Block bazzar | 21.812515,87.228896 | 1300 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 65 | 65 | 0 | 0 | 0 | 65 | 2.925 | 1 | 2.925 | 5 | 0 | 1430 | 0 | 0 | 13 | 1430
8 | Balasore | C | Jaleswar | NAC | 10 | Santia village road | 3.6 | Nitaipada Senapati house | 21.814594,87.231563 | Bhagabat Nayak | 21.815093,87.232362 | 120 | M |  |  |  | Y | SS | 20 | 8 |  | Existing lt line |  | 6 | 6 | 0 | 0 | 0 | 6 | 0.27 | 1 | 0.27 | 3 | 132 | 0 | 0 | 0 | 1 | 132
9 | Balasore | C | Jaleswar | NAC | 10 | Adibasi sahi | 3.4 | Udyana bhabana | 21.816662,87.236997 | Sankar Tudu | 21.817912,87.237812 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
10 | Balasore | C | Jaleswar | NAC | 10 | Udyana bhabana to Sankar Sahu house | 3.5 | Udyana bhabana | 21.817845,87.238245 | Santia village | 21.815785,87.238335 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
11 | Balasore | C | Jaleswar | NAC | 10 | Paltu Barmo village road | 3.5 | Paltu barmo | 21.813328,87.237283 | Mrutyunjaya Jena house | 21.812406,87.237917 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
12 | Balasore | C | Jaleswar | NAC | 10 | Santia village road to Santia railway station | 3 | Haris Rana | 21.812007,87.237137 | Santia railway gate | 21.811317,87.238514 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
13 | Balasore | C | Jaleswar | NAC | 10 | Santia village to Dasa sahi | 3.5 | Starting point | 21.810342,87.236375 | Dasa sahi | 21.808762,87.232552 | 1000 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 37 | 37 | 0 | 37 | 0 | 0 | 3.33 | 1 | 3.33 | 5 | 0 | 1100 | 0 | 0 | 7 | 1100
14 | Balasore | C | Jaleswar | NAC | 12 | NH-60 | 20 | Nuabazzar chhack | 21.806480,87.244979 | Jangalpur | 21.782954,87.219675 | 4000 | 2W |  | Y |  |  | DS | 27 | 9 |  | Existing street light pole | Due to Higher Divider Width - Both Side Pole Arrangement Proposed | 296 | 296 | 0 | 296 | 0 | 0 | 26.64 | 3 | 8.88 | 12 | 0 | 0 | 0 | 8800 | 59 | 8800
15 | Balasore | C | Jaleswar | NAC | 12 | Nuabazzar chhack | 4.5 | Nuabazzar chhack | 21.807351,87.244775 | NH60 | 21.806497,87.244969 | 150 | M |  |  | Y |  | SS | 20 | 8 |  | Do |  | 8 | 8 | 0 | 0 | 8 | 0 | 0.56 | 1 | 0.56 | 3 | 165 | 0 | 0 | 0 | 2 | 165
16 | Balasore | C | Jaleswar | NAC | 5 | Jamalpur road | 3.5 | Starting point | 21.782975,87.219738 | Chaitan Sahu house | 21.792188,87.223606 | 2200 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light |  | 110 | 110 | 0 | 0 | 110 | 0 | 7.7 | 1 | 7.7 | 12 | 0 | 0 | 0 | 2420 | 22 | 2420
17 | Balasore | C | Jaleswar | NAC | 13 | Nadika chhack | 4 | Nadika chhack | 21.795365,87.230266 | NH60 | 21.789834,87.231023 | 900 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 33 | 33 | 0 | 33 | 0 | 0 | 2.97 | 1 | 2.97 | 5 | 0 | 990 | 0 | 0 | 7 | 990
1 | Bhadrak | C | Bhadrak | Municipality |  | NH | 11 | Over bridge | 21.063148,86.494121 | Ending point | 21.059652,86.493605 | 400 | M |  | Y |  |  | DS-Z-Z | 36 | 9 |  | Existing street light pole | Double side pole arrangement | 22 | 22 | 0 | 22 | 0 | 0 | 1.98 | 1 | 1.98 | 3 | 880 | 0 | 0 | 0 | 4 | 880
2 | Bhadrak | C | Bhadrak | Municipality |  | NH | 7 | Motel chhack | 21.069182,86.496356 | Ending point | 21.072005,86.498933 | 300 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 11 | 11 | 0 | 11 | 0 | 0 | 0.99 | 1 | 0.99 | 3 | 330 | 0 | 0 | 0 | 2 | 330
3 | Bhadrak | C | Bhadrak | Municipality |  | NH | 8 | Railway over bridge | 21.101825,86.531177 | Charampa | 21.088961,86.520526 | 2000 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 74 | 74 | 0 | 74 | 0 | 0 | 6.66 | 1 | 6.66 | 12 | 0 | 0 | 0 | 2200 | 15 | 2200
1 | Bhadrak | C | Chandbali | NAC | 1-2 | BHADRAK-CHANDBALI ROAD | 12 | NAC OFFICE | 20.778100,86.744488 | MOURIA CHAKA | 20.710397,86.760752 | 4200 | M |  | Y |  |  | DS-Z-Z | 36 | 9 |  | Existing street light pole |  | 234 | 234 | 0 | 234 | 0 | 0 | 21.06 | 3 | 7.02 | 12 | 0 | 0 | 0 | 9240 | 47 | 9240
2 | Bhadrak | C | Chandbali | NAC | 3-4 | CHANDBALI COLLAGE ROAD | 4 | CHANDBALI COLLAGE CHHAKA | 20.787322,86.754227 | BALIGAOUN PANCHAYATA CHHAKA | 20.782624,86.730288 | 2600 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 130 | 130 | 0 | 0 | 130 | 0 | 9.1 | 2 | 4.55 | 7.5 | 0 | 0 | 2860 | 0 | 26 | 2860
3 | Bhadrak | C | Chandbali | NAC | 15 | CHANDBALI-AARADI ROAD (ORASAHI ROAD) | 4.2 | BALIGAOUN | 20.782622,86.738689 | MAA DURGA TEMPLE | 20.775880,86.738689 | 1200 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 60 | 60 | 0 | 0 | 60 | 0 | 4.2 | 1 | 4.2 | 7.5 | 0 | 0 | 1320 | 0 | 12 | 1320
4 | Bhadrak | C | Chandbali | NAC | 10 | CHANDBALI-AARADI ROAD (ORASAHI ROAD) | 4 |  | 20.774232,86.751765 | KANDHA CHHAKA | 20.762956,86.768216 | 2200 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING LT LINE |  | 110 | 110 | 0 | 0 | 110 | 0 | 7.7 | 1 | 7.7 | 12 | 0 | 0 | 0 | 2420 | 22 | 2420
5 | Bhadrak | C | Chandbali | NAC | 8-10 | KANDHA VILLAGE ROAD | 4 | KANDHA CHHAKA (CHANDBALI ROAD) | 20.762874,86.768174 | KANDHA VILLAGE | 20.755192,86.760502 | 2400 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING LT LINE |  | 120 | 120 | 0 | 0 | 120 | 0 | 8.4 | 2 | 4.2 | 7.5 | 0 | 0 | 2640 | 0 | 24 | 2640
6 | Bhadrak | C | Chandbali | NAC | 9 | CHANDBALI-DHAMARA ROAD (BEANTALPUR VILLAGE ROAD) | 4 | KANDHA CHHAKA | 20.762952,86.763104 | BEANTALPUR VILLAGE | 20.757960,86.774149 | 950 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 48 | 48 | 0 | 0 | 48 | 0 | 3.36 | 1 | 3.36 | 5 | 0 | 1045 | 0 | 0 | 10 | 1045
7 | Bhadrak | C | Chandbali | NAC |  | KANDHA VILLAGE ROAD | 3 | BAITARANI REVER SIDE | 20.757087,86.761447 | HANUMAN MANDIR | 20.764944,86.764164 | 470 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 24 | 24 | 0 | 0 | 0 | 24 | 1.08 | 1 | 1.08 | 3 | 517 | 0 | 0 | 0 | 5 | 517
8 | Bhadrak | C | Chandbali | NAC | 7 | CUTTACK- CHANDIKHOL ROAD | 6 | PAPU SAW MILL | 20.770554,86.730145 | CHANDBALI BRIDGE | 20.764000,86.721846 | 1300 | M |  | Y |  |  | SS | 27 | 9 |  | EXEXISTING STREET LIGHT POLE |  | 48 | 48 | 0 | 48 | 0 | 0 | 4.32 | 1 | 4.32 | 7.5 | 0 | 0 | 1430 | 0 | 10 | 1430
9 | Bhadrak | C | Chandbali | NAC | 7-14 | MEENTARA VILLAGE ROAD | 3 | TARINI CHHAKA | 20.769810,86.727042 | BKGP HIGHSCHOOL | 20.771518,86.719860 | 950 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 48 | 48 | 0 | 0 | 0 | 48 | 2.16 | 1 | 2.16 | 3 | 1045 | 0 | 0 | 0 | 10 | 1045
10 | Bhadrak | C | Chandbali | NAC | 7-14 | PAHADPUR VILLAGE ROAD | 3 | TARINI CHHAKA | 20.769810,86.727042 | PAHADPUR VILLAGE END |  | 980 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 49 | 49 | 0 | 0 | 0 | 49 | 2.205 | 1 | 2.205 | 3 | 1078 | 0 | 0 | 0 | 10 | 1078
11 | Bhadrak | C | Chandbali | NAC | 13 | VILLAGE ROAD | 4 | DEBENDRA MOHANTY HOUSE | 20.770369,86.713070 | PRAKASH ROUT HOUSE | 20.771610,86.715771 | 470 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE | BRANCHES ROAD | 24 | 24 | 0 | 0 | 0 | 24 | 1.08 | 1 | 1.08 | 3 | 517 | 0 | 0 | 0 | 5 | 517
12 | Bhadrak | C | Chandbali | NAC | 12 | CHANDBALI-AARADI ROAD | 5 | KAUDIA BRIDGE | 20.784096,86.713676 | BASTI CHHAKA | 20.778977,86.720006 | 1190 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1309 | 0 | 0 | 12 | 1309
13 | Bhadrak | C | Chandbali | NAC | 12 | RD ROAD | 3 | RD ROAD | 20.783332,86.723696 | KUNJAKALIKA |  | 980 | M |  | Y |  |  | SS | 27 | 9 |  | EXISTING STREET LIGHT POLE |  | 36 | 36 | 0 | 36 | 0 | 0 | 3.24 | 1 | 3.24 | 5 | 0 | 1078 | 0 | 0 | 7 | 1078
14 | Bhadrak | C | Chandbali | NAC | 3 | BADA OSTIA VILLAGE ROAD | 5 | COLLAGE ROAD | 20.790684,86.737925 | NAYAHATA | 20.793806,86.738051 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
15 | Bhadrak | C | Chandbali | NAC | 3 | NAYAHATA VILLAGE ROAD | 4 | STARTING POINT | 20.795805,86.739412 | ENDING POINT |  | 170 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 9 | 9 | 0 | 0 | 0 | 9 | 0.405 | 1 | 0.405 | 3 | 187 | 0 | 0 | 0 | 2 | 187
16 | Bhadrak | C | Chandbali | NAC | 3 | GOPALPUR VILLAGE ROAD | 3 | COLLAGE ROAD | 20.795042,86.743632 | VILLAGE END | 20.797964,86.744286 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
17 | Bhadrak | C | Chandbali | NAC | 1 | VILLAGE ROAD | 3 | CHANDBALI KUANSHAR CHAKA | 20.798192,86.758672 | MAJHI GAOUN | 20.795414,86.773387 | 1800 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 90 | 90 | 0 | 0 | 0 | 90 | 4.05 | 1 | 4.05 | 7.5 | 0 | 0 | 1980 | 0 | 18 | 1980
18 | Bhadrak | C | Chandbali | NAC | 1 | VILLAGE ROAD | 3 | MAJHI GAOUN CHHAKA | 20.794503,86.772888 | VILLAGE END | 20.792192,86.776714 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE | NEED A HIMAX ON THE JOINT OF THIS VILLAGE AND NEXT VILLAGE | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
19 | Bhadrak | C | Chandbali | NAC | 1 | VILLAGE ROAD | 3 | MAJHI GAOUN | 20.792192,86.776714 | VILLAGE END |  | 250 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING STREET LIGHT POLE |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
1 | Mayurbhanj | C | Karanjia | NAC | 12 | Nausahi Village Road | 3 | Soubhagya Panda House | 21.753172,85.969390 | Bansidhar Kamile House | 21.752888,85.968866 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
2 | Mayurbhanj | C | Karanjia | NAC | 8 | Sarpada Road | 8.5 | NH Chhack (Bypass) | 21.752310,85.971627 | Deo River | 21.742654,85.969548 | 1100 | M |  | Y |  |  | SS | 27 | 9 |  | Existing Street Light Pole |  | 41 | 41 | 0 | 41 | 0 | 0 | 3.69 | 1 | 3.69 | 5 | 0 | 1210 | 0 | 0 | 8 | 1210
3 | Mayurbhanj | C | Karanjia | NAC | 8-1 | Jasipur Road | 8.5 | NH Chhack (Bypass) | 21.752289,85.971780 | Hero Showroom | 21.778560,85.982434 | 3300 | M |  | Y |  |  | SS | 27 | 9 |  | Existing Street Light Pole |  | 122 | 122 | 0 | 122 | 0 | 0 | 10.98 | 2 | 5.49 | 7.5 | 0 | 0 | 3630 | 0 | 24 | 3630
4 | Mayurbhanj | C | Karanjia | NAC | 2-3 | Karadia Road | 5 | Narendra Singh House | 21.764326,85.979976 | Natel House | 21.765130,85.985540 | 650 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 33 | 33 | 0 | 0 | 0 | 33 | 1.485 | 1 | 1.485 | 3 | 715 | 0 | 0 | 0 | 7 | 715
5 | Mayurbhanj | C | Karanjia | NAC | 8 | Godisahi to Deo River | 4 | Godisahi Sahadev house | 21.751755,85.975773 | End Point | 21.747055,85.977996 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
1 | Angul | B | Athmallik | NAC | 6 | Manikpur village road | 6 | Manikapathara chhack | 20.737010,84.520406 | Manika pathara bridge | 20.739843,84.511244 | 750 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 28 | 28 | 0 | 28 | 0 | 0 | 2.52 | 1 | 2.52 | 5 | 0 | 825 | 0 | 0 | 6 | 825
2 | Angul | B | Athmallik | NAC | 1 | Girad ghat | 4 | Starting point | 20.732870,84.526817 | Ending point | 20.740153,84.528270 | 900 | M |  |  |  | Y | Ss | 20 | 8 |  | Do |  | 45 | 45 | 0 | 0 | 0 | 45 | 2.025 | 1 | 2.025 | 3 | 990 | 0 | 0 | 0 | 9 | 990
3 | Angul | B | Athmallik | NAC | 6 | Manikapathara road to Liptinga | 3.5 | Manikapathara road | 20.721732,84.525646 | Liptinga | 20.732633,84.526720 | 1500 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 75 | 75 | 0 | 0 | 0 | 75 | 3.375 | 1 | 3.375 | 5 | 0 | 1650 | 0 | 0 | 15 | 1650
4 | Angul | B | Athmallik | NAC | 3 | Tangianisa village road | 4 | Starting point | 20.733930,84.555764 | Fakirpada chhack | 20.742235,84.572914 | 2400 | M |  |  |  | Y | Ss | 20 | 8 |  | Do |  | 120 | 120 | 0 | 0 | 0 | 120 | 5.4 | 2 | 2.7 | 5 | 0 | 2640 | 0 | 0 | 24 | 2640
5 | Angul | B | Athmallik | NAC | 3 | Padma pokhari village road | 3 | Mankadakhenda chhack | 20.739234,84.563894 | Sidhapur chhack | 20.744094,84.567643 | 1000 | M |  |  |  | Y | Ss | 20 | 8 |  | Do |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
6 | Angul | B | Athmallik | NAC | 3 | Badisahi village road | 4 | Tangianisa chhack | 20.732591,84.558330 | Badisahi chhack | 20.732646,84.559769 | 1200 | M |  |  |  | Y | Ss | 20 | 8 |  | Do | Village branch | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
7 | Angul | B | Athmallik | NAC | 3-11 | Baratikra village road | 4 | Harijana sahi | 20.731793,84.556435 | Bartikra chhack | 20.721548,84.551542 | 1400 | M |  |  |  | Y | Ss | 20 | 8 |  | Existing transformer |  | 70 | 70 | 0 | 0 | 0 | 70 | 3.15 | 1 | 3.15 | 5 | 0 | 1540 | 0 | 0 | 14 | 1540
8 | Angul | B | Athmallik | NAC | 11 | Baragaan Tikirasahi | 3 | Baragaan chhack | 20.717595,84.549904 | Mahanadi river | 20.709573,84.547608 | 1100 | M |  |  |  | Y | Ss | 20 | 8 |  | Do |  | 55 | 55 | 0 | 0 | 0 | 55 | 2.475 | 1 | 2.475 | 5 | 0 | 1210 | 0 | 0 | 11 | 1210
9 | Angul | B | Athmallik | NAC | 4 | Rajabhati village road | 3.5 | Rajabhati road | 20.724036,84.545970 | Harijana sahi | 20.727518,84.545715 | 500 | M |  |  |  | Y | Ss | 20 | 8 |  | Existing street light |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
10 | Angul | B | Athmallik | NAC | 9 | Rameswar patana village road | 3.5 | Starting point | 20.715269,84.532852 | Chourighat | 20.707729,84.529462 | 1000 | M |  |  |  | Y | Ss | 20 | 8 |  | Existing lt line |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
11 | Angul | B | Athmallik | NAC | 10 | Smasanghat village road | 3.5 | Smasanghat | 20.708886,84.534942 | Ending point | 20.712989,84.539235 | 850 | M |  |  |  | Y | Ss | 20 | 8 |  | Do |  | 43 | 43 | 0 | 0 | 0 | 43 | 1.935 | 1 | 1.935 | 3 | 935 | 0 | 0 | 0 | 9 | 935
12 | Angul | B | Athmallik | NAC | 10-5 | Purunagard village road | 3 | Starting point | 20.714228,84.540191 | Damasahi | 20.719045,84.540568 | 550 | M |  |  |  | Y | Ss | 20 | 8 |  | Do |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 605 | 0 | 0 | 0 | 6 | 605
13 | Angul | B | Athmallik | NAC | 7 | Liptinga village road | 3.5 | Starting point | 20.721737,84.527303 | Mahanadi bridge | 20.717120.84.526025 | 500 | M |  |  |  | Y | Ss | 20 | 8 |  | Do |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
14 | Angul | B | Athmallik | NAC | 7 | Puleswar | 3 | Puleswar chhack | 20.721423,84.523830 | Water tank | 20.716870,84.509673 | 1600 | M |  |  |  | Y | Ss | 20 | 8 |  | Do |  | 80 | 80 | 0 | 0 | 0 | 80 | 3.6 | 1 | 3.6 | 5 | 0 | 1760 | 0 | 0 | 16 | 1760
1 | Dhenkanal | A | Bhuban | NAC | 2 | Tiora colony road | 3.5 | Starting point | 20.903923,85.835348 | Bhalukhai colony U.P school | 20.903940,85.835348 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
2 | Dhenkanal | A | Bhuban | NAC | 2 | NH 53 | 6 | Near petrol pump | 20.894416,85.833152 | Baunshakana village |  | 2500 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 125 | 125 | 0 | 0 | 125 | 0 | 8.75 | 2 | 4.375 | 7.5 | 0 | 0 | 2750 | 0 | 25 | 2750
3 | Dhenkanal | A | Bhuban | NAC | 2 | Bhalukhai colony - chandi temple | 7 | Bhalukhai Chandika sahi | 20.904336,85.834024 | Chandi temple | 20.905054,85.827761 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
4 | Dhenkanal | A | Bhuban | NAC | 2 | Chandi temple-Womens college | 7 | Chandi temple | 20.905054,85.827761 | Bhubna womens colege | 20.893897,85.828393 | 2000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 100 | 100 | 0 | 0 | 0 | 100 | 4.5 | 1 | 4.5 | 7.5 | 0 | 0 | 2200 | 0 | 20 | 2200
5 | Dhenkanal | A | Bhuban | NAC | 3 | Godipatana__ Budheswar temple | 7 | Godipatana | 20.879481,85.820933 | Budheswar temple | 20.870550,85.829578 | 1400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 70 | 70 | 0 | 0 | 0 | 70 | 3.15 | 1 | 3.15 | 5 | 0 | 1540 | 0 | 0 | 14 | 1540
6 | Dhenkanal | A | Bhuban | NAC | 13 | Chendera pond - Smasan ghaat | 4 | Chendera pond | 20.876833,85.835092 | Smasan ghaat |  | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
7 | Dhenkanal | A | Bhuban | NAC | 14-15 | Astasambhu temple - Padma pokhari | 5 | Astasambhu temple | 20.877788,85.841292 | Padma Pokhari | 20.878694,85.837686 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole | smasan ghaat is near the temple | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
1 | Dhenkanal | A | Kamakhyanagr | NAC | 14 | Rekula Hadabhanga main road | 6.6 | Hadabhanga road | 20.918486,85.542408 | School chhack | 20.920738,85.539320 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
2 | Dhenkanal | A | Kamakhyanagr | NAC | 14 | Puruna Rekula village | 6 | Starting point | 20.920800,85.538403 | Shiva mandira road | 20.926079,85.538354 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Lt line |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
3 | Dhenkanal | A | Kamakhyanagr | NAC | 8 | Shiva mandira Rekula road | 5 | Starting point | 20.926079,85.538381 | Ending point | 20.929370,85.541014 | 550 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Lt line |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 605 | 0 | 0 | 0 | 6 | 605
4 | Dhenkanal | A | Kamakhyanagr | NAC | 6 | Shiva mandira Rekula road | 5 | Starting point | 20.926138,85.538402 | Alutuma chhack | 20.929269,85.537924 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
5 | Dhenkanal | A | Kamakhyanagr | NAC | 2-1 | Budhi padhini village road | 4 | Budhi padhini | 20.931374,85.543669 | Induour village road | 20.922707,85.551367 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
6 | Dhenkanal | A | Kamakhyanagr | NAC | 11 | Khuntapasi badabila village road | 3 | Khuntapasi road | 20.938255,85.524551 | Badabila harijana sahi | 20.933224,85.520828 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
7 | Dhenkanal | A | Kamakhyanagr | NAC | 11 | NH-53 | 6 | Badabila chhack | 20.931423,85.521346 | Dharmasala chhack | 20.932199,85.525137 | 400 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 15 | 15 | 0 | 15 | 0 | 0 | 1.35 | 1 | 1.35 | 3 | 440 | 0 | 0 | 0 | 3 | 440
1 | Keonjhar | C | Anandapur | Municipality | 2 | Bandha pokhori road | 4 | Bandha pokhori | 21.215656,86.127168 | Padmapur puruna sahi | 21.223529,86.132073 | 750 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 38 | 38 | 0 | 0 | 0 | 38 | 1.71 | 1 | 1.71 | 3 | 825 | 0 | 0 | 0 | 8 | 825
2 | Keonjhar | C | Anandapur | Municipality | 2 | Padmapur to Utereswar road | 4 | Nirakara Sahoo house | 21.224464,86.139548 | Near utereswar temple | 21.225931,86.139613 | 2000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 100 | 100 | 0 | 0 | 0 | 100 | 4.5 | 1 | 4.5 | 7.5 | 0 | 0 | 2200 | 0 | 20 | 2200
3 | Keonjhar | C | Anandapur | Municipality | 7 | Dhaneswar pitha road | 4 | Near Utereswar temple | 21.217541,86.137382 | Dhaneipitha | 21.218751,86.1344971 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | New phase to be installed | Under constraction road | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
4 | Keonjhar | C | Anandapur | Municipality | 2-1 | Way to Ganda road | 3.5 | Lambodhara Sahoo house | 21.227855,86.137283 | Near Satyanarayan high school | 21.230437,86.138113 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
5 | Keonjhar | C | Anandapur | Municipality | 1 | Padmapur nua sahi road | 4 | Chintamani Behera | 21.233913,86.142727 | Janghar chhack | 21.240246,86.149002 | 1000 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 50 | 50 | 0 | 0 | 50 | 0 | 3.5 | 1 | 3.5 | 5 | 0 | 1100 | 0 | 0 | 10 | 1100
6 | Keonjhar | C | Anandapur | Municipality | 1 | Birala chhack to Padmapur nuasahi | 4.5 | Birbala chhack |  | Nuasahi | 21.236512,86.139868 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
7 | Keonjhar | C | Anandapur | Municipality | 2 | Panda sahi road | 3.5 | Adina Behera house | 21.233752,86.13110 | Bhagirathi Sahoo | 21.236427,86.128451 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
8 | Keonjhar | C | Anandapur | Municipality | 2 | Anandapur to Karanjia road | 7 | Padmapur gate chhack | 21.236530,86.126054 | Anandapur jail | 21.224095,86.121057 | 1600 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 59 | 59 | 0 | 59 | 0 | 0 | 5.31 | 1 | 5.31 | 7.5 | 0 | 0 | 1760 | 0 | 12 | 1760
9 | Keonjhar | C | Anandapur | Municipality | 2 | Padmapur puruna sahi village road | 4 | Madhaba Sahoo house | 21.228087,86.129784 | NH53 | 21.230693,86.125813 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
10 | Keonjhar | C | Anandapur | Municipality | 3 | Ring bandha Anandapur | 7 | Brahmin debi up school | 21.217595,86.118605 | Baitarini ring road | 21.208727,86.132835 | 2000 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 74 | 74 | 0 | 74 | 0 | 0 | 6.66 | 1 | 6.66 | 12 | 0 | 0 | 0 | 2200 | 15 | 2200
11 | Keonjhar | C | Anandapur | Municipality | 7-9 | Rinf channel road | 4.5 | Starting point | 21.208547,86.133245 | Fakirpur kali bazzar | 21.296304,86.153105 | 2500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 125 | 125 | 0 | 0 | 0 | 125 | 5.625 | 2 | 2.8125 | 5 | 0 | 2750 | 0 | 0 | 25 | 2750
12 | Keonjhar | C | Anandapur | Municipality | 11 | Ring bhandha road | 4.5 | Nepala saha,Chindri sahi | 21.190419,86.162165 | Footbal field |  | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
13 | Keonjhar | C | Anandapur | Municipality | 11 | Mochinda-Fakir pur road | 4 | Balunkeswar chhack | 21.196039,86.163723 | NH53 | 21.203169,86.168478 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
14 | Keonjhar | C | Anandapur | Municipality | 11 | NH 53 | 10 | NH53 | 21.203169,86.168478 | Fakirpur hata | 21.205201,86.156565 | 1200 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 44 | 44 | 0 | 44 | 0 | 0 | 3.96 | 1 | 3.96 | 5 | 0 | 1320 | 0 | 0 | 9 | 1320
15 | Keonjhar | C | Anandapur | Municipality | 10 | Salabani village road | 6 | Salabani village road | 21.205645,86.155694 | Salabani road | 21.212050,86.156728 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
16 | Keonjhar | C | Anandapur | Municipality | 10-11 | Jena sahi road | 3.5 | Salabani hata | 21.205097,86.156617 | Jamjhatiasahi | 21.198344,86.156373 | 900 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 45 | 45 | 0 | 0 | 0 | 45 | 2.025 | 1 | 2.025 | 3 | 990 | 0 | 0 | 0 | 9 | 990
17 | Keonjhar | C | Anandapur | Municipality | 9-6 | Village road | 3.5 | Harijana sahi | 21.201504,86.153841 | Salabani chhack | 21.205445,86.154855 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
18 | Keonjhar | C | Anandapur | Municipality | 6 | Patakul sahi road | 3 | Anil Sahoo house |  | Dalai house |  | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
1 | Keonjhar | C | Keonjharghar | Municipality | 18 | KAMARGARH VILLAGE ROAD | 3 | STARTING POINT | 21.653585,85.611635 | GAMHARIA | 21.660190.85.614339 | 750 | M |  |  |  | Y | SS | 20 | 8 |  | EXISTING TRANSFORMER |  | 38 | 38 | 0 | 0 | 0 | 38 | 1.71 | 1 | 1.71 | 3 | 825 | 0 | 0 | 0 | 8 | 825
2 | Keonjhar | C | Keonjharghar | Municipality | 18-21 | TULASIPUR | 7 | GAMHARIA | 21.665980,85.611976 | TULASIPUR VILLAGE ROAD | 21.670601,85.612307 | 550 | M |  | Y |  |  | SS | 27 | 9 |  | EXISTING STREET LIGHT POLE |  | 20 | 20 | 0 | 20 | 0 | 0 | 1.8 | 1 | 1.8 | 3 | 605 | 0 | 0 | 0 | 4 | 605
3 | Keonjhar | C | Keonjharghar | Municipality | 21 | TULASIPUR VILLAGE ROAD | 3 | STARTING POINT | 21.620273,85.612288 | ENDING POINT | 21.670045,85,613359 | 130 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 7 | 7 | 0 | 0 | 0 | 7 | 0.315 | 1 | 0.315 | 3 | 143 | 0 | 0 | 0 | 1 | 143
4 | Keonjhar | C | Keonjharghar | Municipality | 21 | TULASIPUR MEDICAL COLLAGE ROAD | 4 | STARTING POINT | 21.669751,85.612223 | COLLAGE CHHACK | 21.672138,85.606265 | 700 | M |  |  | Y |  | SS | 20 | 8 |  | EXISTING TRANSFORMER |  | 35 | 35 | 0 | 0 | 35 | 0 | 2.45 | 1 | 2.45 | 5 | 0 | 770 | 0 | 0 | 7 | 770
5 | Keonjhar | C | Keonjharghar | Municipality | 17 | KEONJHAR MAIN ROAD | 9 | INFRONT OF N.H OFFICE | 21.645813,85.617876 | GHUTUR CHHACK | 21.653246,85.630707 | 1600 | M | Y |  |  |  | SS | 27 | 9 |  | DO |  | 59 | 59 | 59 | 0 | 0 | 0 | 7.08 | 1 | 7.08 | 12 | 0 | 0 | 0 | 1760 | 12 | 1760
6 | Keonjhar | C | Keonjharghar | Municipality | 2 | MUMBAI TO KALKATA HIGH WAY | 9 | NEW BUS STAND | 21.631909,85.581946 | FIRE STATION | 21.629477,85.573124 | 1100 | M | Y |  |  |  | SS | 27 | 9 |  | EXISTING STREET LIGHT POLE |  | 41 | 41 | 41 | 0 | 0 | 0 | 4.92 | 1 | 4.92 | 7.5 | 0 | 0 | 1210 | 0 | 8 | 1210
7 | Keonjhar | C | Keonjharghar | Municipality | 2 | MUMBAI TO KALKATA HIGH WAY | 5 | BAIDYARAJ VILLAGE ROAD START | 21.631770,85.575347 | BAIDYARAJ VILLAGE ROAD END | 21.629947,85.578615 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | DO |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
8 | Keonjhar | C | Keonjharghar | Municipality | 6 | BADA SASANA VILLAGE ROAD | 4 | STARTING POINT | 21.633361,85.595068 | HP GAS GODAM | 21.632947,85595623 | 380 | M |  |  |  | Y | SS | 20 | 8 |  | DO | VILLAGE BRANCH ROAD | 19 | 19 | 0 | 0 | 0 | 19 | 0.855 | 1 | 0.855 | 3 | 418 | 0 | 0 | 0 | 4 | 418
9 | Keonjhar | C | Keonjharghar | Municipality | 10 | MANDUA NH 215 | 14 | LADGE | 21.629071,85.622935 | S.P. MARBEL SHOP | 21.628478,85.627732 | 500 | 2W | Y |  |  |  | M | 27 | 9 |  | DO | Center pole arrangement | 19 | 19 | 38 | 0 | 0 | 0 | 4.56 | 1 | 4.56 | 7.5 | 0 | 0 | 550 | 0 | 4 | 550
10 | Keonjhar | C | Keonjharghar | Municipality | 10 | KEONJHAR GHATAGAON ROAD | 10 | PANCHAYATA OFFICE | 21.628437,85.627840 | RAILWAY BRIDGE | 21.623790,85.638636 | 1300 | M | Y |  |  |  | DS-Z-Z | 36 | 9 |  | Existing street light pole | Double side pole arrangement | 72 | 72 | 72 | 0 | 0 | 0 | 8.64 | 1 | 8.64 | 12 | 0 | 0 | 0 | 2860 | 14 | 2860
1 | Jharsuguda | B | Belpahar | Municipality | 16 | Maharanapada village road | 3 | Maharanapada | 21.782742,83.868647 | Bandhbahal road | 21.781456,83.873062 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
2 | Jharsuguda | B | Belpahar | Municipality | 16 | Jurabagh road | 7 | Mujbal chhack | 21.793357,83.869205 | RCP chhack | 21.783490,83.864237 | 1500 | M |  |  | Y |  | SS | 27 | 9 |  | Existing transformer |  | 56 | 56 | 0 | 0 | 56 | 0 | 3.92 | 1 | 3.92 | 5 | 0 | 1650 | 0 | 0 | 11 | 1650
3 | Jharsuguda | B | Belpahar | Municipality | 16 | Sunday market to Kadelmunda | 4 | Sunday market | 21.784913,83.864250 | Makarchat chhack | 21.792041,83.853064 | 1700 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 85 | 85 | 0 | 0 | 0 | 85 | 3.825 | 1 | 3.825 | 5 | 0 | 1870 | 0 | 0 | 17 | 1870
4 | Jharsuguda | B | Belpahar | Municipality | 18 | Vivekananda school road | 4 | Vivekananda school | 21.798087,83.855806 | Makarchat | 21.789952,83.844195 | 2000 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 100 | 100 | 0 | 0 | 0 | 100 | 4.5 | 1 | 4.5 | 7.5 | 0 | 0 | 2200 | 0 | 20 | 2200
5 | Jharsuguda | B | Belpahar | Municipality | 18 | Makarchat village road | 4.5 | Makarchat chhack | 21.793715,83.854618 | Smasan | 21.792596,83.841020 | 1600 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 80 | 80 | 0 | 0 | 0 | 80 | 3.6 | 1 | 3.6 | 5 | 0 | 1760 | 0 | 0 | 16 | 1760
6 | Jharsuguda | B | Belpahar | Municipality | 7-18 | Udajahajpada village road | 4.5 | Udajahajapad chhack | 21.800735,83.853116 | Ghhicha ghat | 21.812135,83.847676 | 2000 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 100 | 100 | 0 | 0 | 0 | 100 | 4.5 | 1 | 4.5 | 7.5 | 0 | 0 | 2200 | 0 | 20 | 2200
7 | Jharsuguda | B | Belpahar | Municipality | 6 | Ghhicha Ghat village road | 10.5 | Ghhicha ghat chhack | 21.812298,83.848272 | Alok treders | 21.816571,83.858140 | 1300 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 48 | 48 | 0 | 48 | 0 | 0 | 4.32 | 1 | 4.32 | 7.5 | 0 | 0 | 1430 | 0 | 10 | 1430
8 | Jharsuguda | B | Belpahar | Municipality | 6-3 | Jagannath mandira village road | 7 | Jagannath mandira | 21.811196,83.848344 | Mahima ashram | 21.813568,83.848315 | 260 | M |  |  | Y |  | SS | 27 | 9 |  | Do |  | 10 | 10 | 0 | 0 | 10 | 0 | 0.7 | 1 | 0.7 | 3 | 286 | 0 | 0 | 0 | 2 | 286
9 | Jharsuguda | B | Belpahar | Municipality | 3 | Baba matha road | 5 | Mahima ashram | 21.815401,83.847978 | Pokhori bandha | 21.814095,83.843583 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
10 | Jharsuguda | B | Belpahar | Municipality | 17 | Milan chhack | 5 | Karlakhama chhack | 21.834452,83.835543 | Dhara munda village | 21.843156,83.827660 | 1800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 90 | 90 | 0 | 0 | 0 | 90 | 4.05 | 1 | 4.05 | 7.5 | 0 | 0 | 1980 | 0 | 18 | 1980
11 | Jharsuguda | B | Belpahar | Municipality | 17 | Mahijore village road | 4 | Mahijore chhack | 21.836511,83.846768 | Chutiapada | 21.842780,83.834959 | 3400 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 170 | 170 | 0 | 0 | 0 | 170 | 7.65 | 2 | 3.825 | 5 | 0 | 3740 | 0 | 0 | 34 | 3740
12 | Jharsuguda | B | Belpahar | Municipality | 17 | Daradhipa village road | 3.5 | Starting point | 21.841313,83.839450 | Ending point | 21.839946,83.836478 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
13 | Jharsuguda | B | Belpahar | Municipality | 17 | Mahijore to Khamarpada | 4 | Maharpada basti | 21.839743,83.846871 | Ending point | 21.839941,83.848546 | 160 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 176 | 0 | 0 | 0 | 2 | 176
14 | Jharsuguda | B | Belpahar | Municipality | 12 | Sani mandira road | 7 | Sani mandira | 21.8255143,83.870675 | Mirdhadera | 21.822912,83.868134 | 400 | M |  |  | Y |  | SS | 27 | 9 |  | Existing transformer |  | 15 | 15 | 0 | 0 | 15 | 0 | 1.05 | 1 | 1.05 | 3 | 440 | 0 | 0 | 0 | 3 | 440
15 | Jharsuguda | B | Belpahar | Municipality | 11 | Mirdhadera road | 4 | Mirdhadera chhack | 21.817620,83.864007 | Eiidhya road | 21.817293,83.866781 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
16 | Jharsuguda | B | Belpahar | Municipality | 11-12 | Khukhel mahal village road | 3.5 | Mahesh Biswal house | 21.814008,83.874151 | Hanuman mandira | 21.815047,83.878044 | 550 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 605 | 0 | 0 | 0 | 6 | 605
17 | Jharsuguda | B | Belpahar | Municipality | 12 | Luhurpada road | 3.5 | Starting point | 21.815659,83.880291 | Ending point | 21.816568,83.880116 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
18 | Jharsuguda | B | Belpahar | Municipality | 12 | Shiva mandira road | 1.5 | Lumbodhar Rohi Das | 21.820811,83.883602 | Shiva mandira | 21.821812,83.88108 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
19 | Jharsuguda | B | Belpahar | Municipality | 12 | Chhualiberna road | 4 | Chhualiberna chhack | 21.829878,83.887659 | Banabhoji chhack | 21.836354,83.888298 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
20 | Jharsuguda | B | Belpahar | Municipality | 12 | Bagmar village road | 3.5 | Starting point | 21.831750,83.889037 | Ending point | 21.834382,83.895592 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
21 | Jharsuguda | B | Belpahar | Municipality | 12 | Chhualiberna basti road | 3.5 | Starting point | 21.823936,83.879850 | Sukhabangha | 21.832838,83.874772 | 1450 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 73 | 73 | 0 | 0 | 0 | 73 | 3.285 | 1 | 3.285 | 5 | 0 | 1595 | 0 | 0 | 15 | 1595
22 | Jharsuguda | B | Belpahar | Municipality | 12,2,5,17 | Gidhghara to Khadiapada main road | 7-10 | Gidhghara chhack | 21.842017,83.881170 | Khadiapada | 21.825301,83.841415 | 7800 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 289 | 289 | 0 | 289 | 0 | 0 | 26.01 | 5 | 5.202 | 7.5 | 0 | 0 | 8580 | 0 | 58 | 8580
23 | Jharsuguda | B | Belpahar | Municipality | 6 | Malipada road | 4 | Malipada chhack | 21.811463,83.856939 | Khalguda | 21.813028,83.844983 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
1 | Jharsuguda | B | Brajrajnagar | Municipality | 5 | Latchkura village road | 4.3 | Starting point | 21.813254,83.921072 | Ending point | 21.811241,83.911424 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
2 | Jharsuguda | B | Brajrajnagar | Municipality | 7 | Gourpada to Rajmohan chhack | 4 | Gourpada chhack | 21.793860,83.922391 | Rajmohan chhack | 21.790515,83.924518 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
c | Jharsuguda | B | Brajrajnagar | Municipality | 7 | Kartikpada village road | 3.2 | Starting point | 21.796611,83.918534 | Ending point | 21.798784,83.919736 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
4 | Jharsuguda | B | Brajrajnagar | Municipality | 7 | Sukupada village road | 3.4 | Starting point | 21.799139,83.919350 | Ending point | 21.800978,83.918065 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
5 | Jharsuguda | B | Brajrajnagar | Municipality | 8 | Bahadur pada road | 4 | Little Angel school | 20.803744,83.931097 | Baidyapada chhack | 21.801540,83.932874 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
6 | Jharsuguda | B | Brajrajnagar | Municipality | 8 | Katabagh road | 4 | Katabagh chhack | 21.797945,83.936219 | Church school | 21.795523,83.939702 | 900 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 45 | 45 | 0 | 0 | 0 | 45 | 2.025 | 1 | 2.025 | 3 | 990 | 0 | 0 | 0 | 9 | 990
7 | Jharsuguda | B | Brajrajnagar | Municipality | 8 | Katabagh Belivers church | 4 | Believers church | 21,799634,83.939072 | Chandi mandira | 21.808151,83.942364 | 3100 | M |  |  | Y |  | SS | 27 | 9 |  | Do |  | 115 | 115 | 0 | 0 | 115 | 0 | 8.05 | 2 | 4.025 | 7.5 | 0 | 0 | 3410 | 0 | 23 | 3410
8 | Jharsuguda | B | Brajrajnagar | Municipality | 16 | Chandi mandira road | 4-7 | Near Believer church | 21.810346,83.936312 | Paper mill | 21.817979,83.931451 | 1200 | M |  |  | Y |  | SS | 27 | 9 |  | Do | Village branch road of 200 m | 44 | 44 | 0 | 0 | 44 | 0 | 3.08 | 1 | 3.08 | 5 | 0 | 1320 | 0 | 0 | 9 | 1320
9 | Jharsuguda | B | Brajrajnagar | Municipality | 16 | Paper mill | 3 | Double storage | 21.818137,83.932800 | Kashmirpada | 21.816847,83.933061 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
10 | Jharsuguda | B | Brajrajnagar | Municipality | 16 | Jharampada village road | 3 | Chandi mandira road | 21.815617,83.932486 | Jharampada | 21.816573,83.934722 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
11 | Jharsuguda | B | Brajrajnagar | Municipality | 19 | Remjha main road | 3 | Starting point | 21.835427,83.937539 | Dumer upper | 21.834201,83.936103 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
12 | Jharsuguda | B | Brajrajnagar | Municipality | 20 | Remjha village to Power housepada | 4.2 | Remjha village | 21.837425,83.4473 | Powerhousepada | 21.838307,83.929093 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
13 | Jharsuguda | B | Brajrajnagar | Municipality | 23 | Brajrajnagar collage main gate | 3.5 | Starting point | 21.847150,83.925491 | Collage area | 21.846415,83.929480 | 500 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 19 | 19 | 0 | 19 | 0 | 0 | 1.71 | 1 | 1.71 | 3 | 550 | 0 | 0 | 0 | 4 | 550
14 | Jharsuguda | B | Brajrajnagar | Municipality | 23 | Khaliakani village end | 7 | Khaliakani starting | 21.850721,83.936091 | Brajrajnagar main road | 21.863406,83.945797 | 3500 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 130 | 130 | 0 | 130 | 0 | 0 | 11.7 | 2 | 5.85 | 7.5 | 0 | 0 | 3850 | 0 | 26 | 3850
15 | Jharsuguda | B | Brajrajnagar | Municipality | 22 | Brajrajnagar main road | 12 | Barghat chhack | 21.863711,83.947468 | Toll gate | 21.861630,83.936436 | 1200 | M |  | Y |  |  | DS-Z-Z | 36 | 9 |  | Do |  | 66 | 66 | 0 | 66 | 0 | 0 | 5.94 | 1 | 5.94 | 7.5 | 0 | 0 | 2640 | 0 | 13 | 2640
16 | Jharsuguda | B | Brajrajnagar | Municipality | 22 | Jharsuguda-Raygada road | 7 | Gandhi chhack | 21.861822,83.923243 | Sai mandira | 21.859112,83.910587 | 1300 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 48 | 48 | 0 | 48 | 0 | 0 | 4.32 | 1 | 4.32 | 7.5 | 0 | 0 | 1430 | 0 | 10 | 1430
17 | Jharsuguda | B | Brajrajnagar | Municipality | 23 | Badheikhatapada village road | 4 | Starting point | 21.859627,83.939396 | Gandghor village road | 21.857071,83.944457 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
18 | Jharsuguda | B | Brajrajnagar | Municipality | 20-23 | Remjha village road | 4 | Gandghora road | 21.851530,83.942762 | Remjha chhack | 21.839263,83.936856 | 1800 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 90 | 90 | 0 | 0 | 0 | 90 | 4.05 | 1 | 4.05 | 7.5 | 0 | 0 | 1980 | 0 | 18 | 1980
19 | Jharsuguda | B | Brajrajnagar | Municipality | 23 | Khalikani Medical chhack | 5 | Khaliakani chhack | 21.849629,83.924611 | Mahavirnagar nala | 21.847114,83.921415 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
20 | Jharsuguda | B | Brajrajnagar | Municipality | 3 | Abhayapur village road | 4.5 | Starting point | 21.842252,83.922787 | Ending point | 21.842085,83.924439 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
21 | Jharsuguda | B | Brajrajnagar | Municipality | 3 | Mundapada village road | 3.5 | Starting point | 21.836879,83.920165 | Ending point | 21.835597,83.919704 | 130 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 7 | 7 | 0 | 0 | 0 | 7 | 0.315 | 1 | 0.315 | 3 | 143 | 0 | 0 | 0 | 1 | 143
22 | Jharsuguda | B | Brajrajnagar | Municipality | 3 | Gurdyarapada village road | 5 | Starting point | 21.837540,83.17616 | Ending point | 21.834919,83.918173 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
23 | Jharsuguda | B | Brajrajnagar | Municipality | 13 | Belpahada old road | 5.5 | Madhubananagar | 21.836600,83.900895 | Chuakani village | 21.839565,83.981450 | 1400 | M |  |  |  | Y | SS | 20 | 8 |  | Do | Khadiapada branch road | 70 | 70 | 0 | 0 | 0 | 70 | 3.15 | 1 | 3.15 | 5 | 0 | 1540 | 0 | 0 | 14 | 1540
24 | Jharsuguda | B | Brajrajnagar | Municipality | 21 | Mahavirnagar viullage road | 4-7 | Mahavirnagar | 21.840048,83.922373 | Mangala mandira | 21.839432,83.925668 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
1 | Sambalpur | B | Kuchinda | NAC | 10-11 | Badapada Village road | 4 | Gate Chhack | 21.762172,84.359068 | Meal House | 21.762928,84.363609 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L .T line |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
2 | Sambalpur | B | Kuchinda | NAC | 11 | Sargid Village Road | 4 | Balbadi School | 21.762124,84.363001 | Pump house | 21.761788,84.366161 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
3 | Sambalpur | B | Kuchinda | NAC | 11 | Sargid village road to river | 3.5 | Sasi Makar house | 21.762780,84.367505 | Ending point | 21.762557,84.368734 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
4 | Sambalpur | B | Kuchinda | NAC | 11 | Tungripada village road | 4 | Bir majhi house | 21.768036,84.368563 | Badkishanpada | 21.775602,84.374473 | 1400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 70 | 70 | 0 | 0 | 0 | 70 | 3.15 | 1 | 3.15 | 5 | 0 | 1540 | 0 | 0 | 14 | 1540
5 | Sambalpur | B | Kuchinda | NAC | 10 | Saida road to Junadihi | 10 | Saida chhack | 21.765902,84.355866 | Club house | 21.761363,84.355507 | 550 | M |  | Y |  |  | SS | 27 | 9 |  | Existing L.T line |  | 20 | 20 | 0 | 20 | 0 | 0 | 1.8 | 1 | 1.8 | 3 | 605 | 0 | 0 | 0 | 4 | 605
6 | Sambalpur | B | Kuchinda | NAC | 10 | Saida road | 6 | Anganbadi | 21.761593,84.353266 | Durjyodhan Nayak house | 21.764382,84.349478 | 1000 | M |  | Y |  |  | SS | 27 | 9 |  | Existing transformer |  | 37 | 37 | 0 | 37 | 0 | 0 | 3.33 | 1 | 3.33 | 5 | 0 | 1100 | 0 | 0 | 7 | 1100
7 | Sambalpur | B | Kuchinda | NAC | 10-9 | Kuchinda-Jharsuguda road | 8 | Check gate chhack | 21.762211,84.359027 | Khundapasi chhack | 21.754680,84.360876 | 900 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light |  | 33 | 33 | 0 | 33 | 0 | 0 | 2.97 | 1 | 2.97 | 5 | 0 | 990 | 0 | 0 | 7 | 990
8 | Sambalpur | B | Kuchinda | NAC | 9 | Nageswarpada | 4 | Kundeswar mandir chhack | 21.753547,84.855757 | Saida nadi | 21.758147,84.355170 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
9 | Sambalpur | B | Kuchinda | NAC | 9 | Kuchinda village road | 4 | Kundapasi chhack | 21.753629,84.357285 | Ramjipada | 21.752384,84.357581 | 130 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 7 | 7 | 0 | 0 | 0 | 7 | 0.315 | 1 | 0.315 | 3 | 143 | 0 | 0 | 0 | 1 | 143
10 | Sambalpur | B | Kuchinda | NAC | 9 | Kusmir road | 7 | Starting point | 21.748596,84.360603 | Ending point | 21.749249,84.363475 | 350 | M |  | Y |  |  | SS | 27 | 9 |  | Existing L.T line |  | 13 | 13 | 0 | 13 | 0 | 0 | 1.17 | 1 | 1.17 | 3 | 385 | 0 | 0 | 0 | 3 | 385
11 | Sambalpur | B | Kuchinda | NAC | 8-9 | Kuchinda-Baneigard road | 7 | Fire station | 21.747890,84.368454 | Narsaripada | 21.747365,84.381977 | 1500 | M |  | Y |  |  | SS | 27 | 9 |  | Existing transformer |  | 56 | 56 | 0 | 56 | 0 | 0 | 5.04 | 1 | 5.04 | 7.5 | 0 | 0 | 1650 | 0 | 11 | 1650
12 | Sambalpur | B | Kuchinda | NAC | 8 | Ghosa mantrimunda road | 4 | Starting point | 21.741938,84.383501 | Ghoisa Sahi | 21.731900,84.378453 | 1300 | M |  |  | Y |  | SS | 20 | 8 |  | Existing L .T line |  | 65 | 65 | 0 | 0 | 65 | 0 | 4.55 | 1 | 4.55 | 7.5 | 0 | 0 | 1430 | 0 | 13 | 1430
13 | Sambalpur | B | Kuchinda | NAC | 8 | Ghosa village road | 3.5 | Kukuda farm | 21.730523,84.378218 | Kishan pada | 21.732467,84.381940 | 750 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 38 | 38 | 0 | 0 | 0 | 38 | 1.71 | 1 | 1.71 | 3 | 825 | 0 | 0 | 0 | 8 | 825
14 | Sambalpur | B | Kuchinda | NAC | 8 | Ghosato Sargodam road | 4 | Gobardhana Sunani house | 21.732131,84.374116 | Dumping chhack | 21.733502,84.368827 | 600 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light |  | 30 | 30 | 0 | 0 | 30 | 0 | 2.1 | 1 | 2.1 | 3 | 660 | 0 | 0 | 0 | 6 | 660
15 | Sambalpur | B | Kuchinda | NAC | 8 | Ghosa road | 4.5 | Starting point | 21.734299,84.365591 | Rabi Pruset house | 21.737161,84.362945 | 550 | M |  |  | Y |  | SS | 20 | 8 |  | Existing village transformer |  | 28 | 28 | 0 | 0 | 28 | 0 | 1.96 | 1 | 1.96 | 3 | 605 | 0 | 0 | 0 | 6 | 605
16 | Sambalpur | B | Kuchinda | NAC | 7 | Kuchinda road | 5 | Bhisa Munda | 21.741533,84.357368 | Sastrinagar | 21.744474,84.354863 | 500 | M |  |  | Y |  | SS | 20 | 8 |  | Existing transformer |  | 25 | 25 | 0 | 0 | 25 | 0 | 1.75 | 1 | 1.75 | 3 | 550 | 0 | 0 | 0 | 5 | 550
17 | Sambalpur | B | Kuchinda | NAC | 7 | Village road | 3 | Bipin Patel house | 21.737952,84.356441 | Shiva mandira | 21.733659,84.352670 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
18 | Sambalpur | B | Kuchinda | NAC | 6 | Jharsuguda-Tileibani road | 7 | Starting point | 21.731872,84.351311 | Ending point | 21.730303,84.352422 | 200 | M |  | Y |  |  | SS | 27 | 9 |  | Existing L .T line |  | 7 | 7 | 0 | 7 | 0 | 0 | 0.63 | 1 | 0.63 | 3 | 220 | 0 | 0 | 0 | 1 | 220
19 | Sambalpur | B | Kuchinda | NAC | 1-2 | Mahuldihi road | 4 | Dolp Sharma house | 21.737618,84.344173 | Mission school | 21.729630,84.340981 | 1100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 55 | 55 | 0 | 0 | 0 | 55 | 2.475 | 1 | 2.475 | 5 | 0 | 1210 | 0 | 0 | 11 | 1210
20 | Sambalpur | B | Kuchinda | NAC | 1 | Talpuda road | 4 | Paesana Bagh house | 21.723310,84.332724 | Dangaghat | 21.721527,84.329336 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
21 | Sambalpur | B | Kuchinda | NAC | 3 | Kiraghat road | 5 | Starting point | 21.743193,84.335109 | Kiraghat | 21.733506,84.323198 | 1900 | M |  |  | Y |  | SS | 20 | 8 |  | Existing school transformer |  | 95 | 95 | 0 | 0 | 95 | 0 | 6.65 | 1 | 6.65 | 12 | 0 | 0 | 0 | 2090 | 19 | 2090
22 | Sambalpur | B | Kuchinda | NAC | 3 | Bazzar road | 5 | Pond | 21.744755,84.343232 | Kali mandira | 21.746373,84.346072 | 350 | M |  |  | Y |  | SS | 20 | 8 |  | Existing transformer |  | 18 | 18 | 0 | 0 | 18 | 0 | 1.26 | 1 | 1.26 | 3 | 385 | 0 | 0 | 0 | 4 | 385
1 | Ganjam | A | Aska | NAC | 12 | I B Road | 5.5 | Starting Point | 19.613154,84.667707 | Kenal Road | 19.610729,84.669574 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
2 | Ganjam | A | Aska | NAC | 12 | Badanadi road | 3.5 | Alipur Road | 19.616291,84.666649 | Santoshi Maa Marathi Basha | 19.620272,84.665272 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
3 | Ganjam | A | Aska | NAC | 12 | ACMPCS Back side colony | 3.5 | NH-157 | 19.616722,84.664762 | End Point | 19.620251,84.665251 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
4 | Ganjam | A | Aska | NAC | 18 | pakela Palli Road | 4.5 | Starting Point | 19.625256,84.654693 | End Point | 19.625257,84.655471 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
5 | Ganjam | A | Aska | NAC | 17 | Lalasasan (Harijana Sahi) | 6 | Starting Point |  | End Point | 19.622241,84.649218 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
6 | Ganjam | A | Aska | NAC | 9 | Sonambo (Sani Temple Gali) | 3.3 | Starting Point | 19.611013,84.654318 | End Point |  | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
7 | Ganjam | A | Aska | NAC | 9 | Rushikulya Rever Side | 5.5 | Starting Point | 19.610395,84.654296 | End Point |  | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
8 | Ganjam | A | Aska | NAC | 8 | Ganda Palli Back side Road | 4.5 | HP Gas Godown | 19.610137,84.645335 | Bhaskar Das House | 19.610803,84.643558 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
9 | Ganjam | A | Aska | NAC | 8 | Rushikulya Rever Side | 4.5 | Sonambo Smasan | 19.610006,84.651198 | Kali Temple | 19.609734,84.648273 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
10 | Ganjam | A | Aska | NAC | 2-7 | Rushikulya Rever Side | 4.5 | Rushikulya Bridge |  | End Point |  | 2000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 100 | 100 | 0 | 0 | 0 | 100 | 4.5 | 1 | 4.5 | 7.5 | 0 | 0 | 2200 | 0 | 20 | 2200
11 | Ganjam | A | Aska | NAC | 6 | Mrutuanjaya Lane | 3 | Lane no 1 | 19.611125,84.657701 | End Point |  | 100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 5 | 5 | 0 | 0 | 0 | 5 | 0.225 | 1 | 0.225 | 3 | 110 | 0 | 0 | 0 | 1 | 110
12 | Ganjam | A | Aska | NAC | 7 | Sai Mandar Road | 4 | Starting Point |  | End Point |  | 100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 5 | 5 | 0 | 0 | 0 | 5 | 0.225 | 1 | 0.225 | 3 | 110 | 0 | 0 | 0 | 1 | 110
13 | Ganjam | A | Aska | NAC | 15 | Tota Harijan Sahi | 3.5 | Starting Point | 19.612729,84.657846 | End Point | 19.612774,84.657272 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
14 | Ganjam | A | Aska | NAC | 15 | Anganbadi Gali | 3 | Starting Point |  | End Point |  | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
15 | Ganjam | A | Aska | NAC | 13 | kalimukhi Village Road | 3.5 | Kottha Ghar |  | Laxmi Pradhan | 19.612617,84.661757 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
16 | Ganjam | A | Aska | NAC | 5 | Kabristan | 3 | Starting Point |  | End Point |  | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
17 | Ganjam | A | Aska | NAC | 13 | Karansen Park | 3 | Starting Point |  | End Point |  | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
18 | Ganjam | A | Aska | NAC | 11 | Kumbhar Sahi | 3 | Kumbhar Sahi | 19.610810,84.664581 | End Point | 19.610915,84.665283 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
19 | Ganjam | A | Aska | NAC | 11 | Khambeswari temple | 3 | Starting Point |  | End Point |  | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
20 | Ganjam | A | Aska | NAC | 2 | Banivihar Diverssion Road | 4 | Starting Point |  | End Point | 19.607280,84.671475 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
21 | Ganjam | A | Aska | NAC | 2 | Banivihar Village road | 3 | Starting Point |  | End Point |  | 100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street light pole |  | 5 | 5 | 0 | 0 | 0 | 5 | 0.225 | 1 | 0.225 | 3 | 110 | 0 | 0 | 0 | 1 | 110
1 | Ganjam | A | Bhanjanagar | NAC | [13 empty] | SS | 20 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0
1 | Ganjam | A | Chikiti | NAC | 6 | Annapurna Bihar | 7 | Starting Point | 19.204305,84.602486 | End Point | 19.204973,84.602747 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT Pole |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
2 | Ganjam | A | Chikiti | NAC | 6 | Masari Road | 3.5 | Samshan Ghat | 19.203833,84.604049 | End Point | 19.205839,84.604414 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT Pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
3 | Ganjam | A | Chikiti | NAC | 6 | Rusadali Main Road (Dump Yard) | 3.5 | Rusadali | 19.204846,84.601132 | Hanuman Temple | 19.210576,84.603446 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
4 | Ganjam | A | Chikiti | NAC | 9 | Brahma Nagar | 4 | Starting Point | 19.199689,84.599791 | End Point | 19.200220,84.599949 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
5 | Ganjam | A | Chikiti | NAC | 9 | Brahma Nagar | 5 | Near Arjun Panda Sanadika | 19.199095,84.599861 | End Point | 19.198155,84.599663 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
6 | Ganjam | A | Chikiti | NAC | 9 | Brahma Nagar | 7 | Near Arjun Panda Sanadika | 19.199095,84.599861 | End Point | 19.199666,84.598897 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
7 | Ganjam | A | Chikiti | NAC | 9 | Bus Stand Front Road | 4 | Starting Point | 19.201920,84.595940 | End Point |  | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
8 | Ganjam | A | Chikiti | NAC | 9 | Brahma Nagar | 6 | Radhakanta Pradhan House | 19.199753,84.596769 | Canal Bridge | 19.197919,84.595639 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT Pole |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
9 | Ganjam | A | Chikiti | NAC | 7 | Sainagar | 4 | Ras Kamal House | 19.199707,84.605503 | End Point | 19.198284,84.605043 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
10 | Ganjam | A | Chikiti | NAC | 1 | Electric Chhack | 7 | Transformer Office Side | 19.196776,84.612950 | End Point | 19.195985,84.612720 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
11 | Ganjam | A | Chikiti | NAC | 1 | Electric Chhack Lane No 1 | 7 | Lane No 1 | 19.196133,84.612745 | End Point | 19.196055,84.613204 | 100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 5 | 5 | 0 | 0 | 0 | 5 | 0.225 | 1 | 0.225 | 3 | 110 | 0 | 0 | 0 | 1 | 110
12 | Ganjam | A | Chikiti | NAC | 1 | Kumbhar Sahi | 4 | Monali Behara House | 19.200471,84.613388 | Chandrasekhar Temple | 19.201179,84.611979 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
13 | Ganjam | A | Chikiti | NAC | 4 | Panchyat Sameeti Road | 3.5 | Panchyat Sameetri Office | 19.203366,84.644851 | Raj Smashan | 19.205681,84.609748 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
14 | Ganjam | A | Chikiti | NAC | 1 | Maheshwar Nagar | 3.5 | Essar Petrol Pump | 19.194376,84.616821 | Pump House | 19.193774,84.615860 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
15 | Ganjam | A | Chikiti | NAC | 1 | Maheshwar Nagar Lane 1 | 7 | Starting Point | 19.194151,84.616500 | End Point |  | 100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 5 | 5 | 0 | 0 | 0 | 5 | 0.225 | 1 | 0.225 | 3 | 110 | 0 | 0 | 0 | 1 | 110
16 | Ganjam | A | Chikiti | NAC | 1 | Balakumari Temple Road | 3 | NH site | 19.197639,84.615930 | Balakumari Temple | 19.197529,84.615949 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
17 | Ganjam | A | Chikiti | NAC |  | Suguna Hotel | 5 | Suguna Hotel Side Road | 19.199975,84.604253 | End Point |  | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
18 | Ganjam | A | Chikiti | NAC | 7 | Village Road | 5 | Rajan Sahu House | 19.197815,84.601646 | Khani Bondha | 19.196672,84.603503 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
19 | Ganjam | A | Chikiti | NAC | 7 | Panditira Sahi | 4 | Starting Point | 19.197664,84.601215 | Canal Road | 19.198316,84.591441 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
20 | Ganjam | A | Chikiti | NAC | 12 | Palasing road | 5 | Thakurani temple chhack | 19.204534,84.593161 | Kenal road | 19.198316,84.591441 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
21 | Ganjam | A | Chikiti | NAC | 9 | Bramhanagar 1 | 5.3 | Starting Point | 19.199899,84.598491 | End Point | 19.199312,84.598970 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
22 | Ganjam | A | Chikiti | NAC | 9 | Bramhanagar 2 | 5.3 | Starting Point | 19.198943,84.599077 | End Point | 19.199417,84.599294 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
23 | Ganjam | A | Chikiti | NAC | 9 | Bramhanagar 3 | 5.5 | Bibhuprasad Padhi house | 19.200348,84.599104 | End Point | 19.200190,84.599980 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
24 | Ganjam | A | Chikiti | NAC | 1 | Trinathanagar Harijana street | 5.4 | Plot Lane 1 | 19.197939,84.611662 | End Point | 19.197907,84.610263 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
25 | Ganjam | A | Chikiti | NAC | 1 | Transformer office right side | 5.4 | Lane2 | 19.196649,84.613584 | End Point | 19.195758,84.613601 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
1 | Ganjam | A | Polsara | NAC | [13 empty] | SS | 20 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0
1 | Nayagarh | D | Nayagarh | NAC | 3 | Balibandha road | 3 | Start point | 20.139496,85.105296 | Park | 20.141088,85.105296 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
2 | Nayagarh | D | Nayagarh | NAC | 6-7 | Dashapalla- Balangir road(NH-57) | 10 | Sadaka sahi | 20.138095,85.083649 | Chack gate | 20.133452,85.089464 | 1000 | M |  | Y |  |  | DS-Z-Z | 36 | 9 |  | Existing street light pole |  | 56 | 56 | 0 | 56 | 0 | 0 | 5.04 | 1 | 5.04 | 7.5 | 0 | 0 | 2200 | 0 | 11 | 2200
3 | Nayagarh | D | Nayagarh | NAC | 9-10 | Nayagarh-Odagaon road | 12.5 | PTS Chhack | 20.114788,85.101092 | College road | 20.121204,85.103186 | 1000 | M |  | Y |  |  | DS-Z-Z | 36 | 9 |  | Existing street light pole |  | 56 | 56 | 0 | 56 | 0 | 0 | 5.04 | 1 | 5.04 | 7.5 | 0 | 0 | 2200 | 0 | 11 | 2200
4 | Nayagarh | D | Nayagarh | NAC | 9-11 | Nayagarh-Odagaon road | 12.5 | Ram mandra |  | Odagaon Chhack | 20.256876,85.104147 | 500 | M |  |  |  | Y | DS-Z-Z | 36 | 9 |  | Existing street light pole |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 1100 | 0 | 0 | 0 | 6 | 1100
1 | Nayagarh | D | Ranpur | NAC | 15 | Pampada to Mangraj pur | 4 | Pampada | 20.048221,85.353661 | Collage gate | 20.052793,85.358394 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
2 | Nayagarh | D | Ranpur | NAC | 8-14 | Jagannath road | 5 | Starting point | 20.059116,85.355173 | Hero showroom | 20.060065,85.352937 | 300 | M |  |  | Y |  | SS | 20 | 8 |  | Existing transformer |  | 15 | 15 | 0 | 0 | 15 | 0 | 1.05 | 1 | 1.05 | 3 | 330 | 0 | 0 | 0 | 3 | 330
3 | Nayagarh | D | Ranpur | NAC | 8-2 | Machha market road | 4 | Samukasahi | 20.062192,85.348246 | Machha market | 20.070212,85.341929 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
4 | Nayagarh | D | Ranpur | NAC | 2 | Sunakhala road | 6 | Starting point | 20.078729,85.341351 | Campatipur bridge | 20.083200,85.340828 | 600 | M |  |  | Y |  | SS | 20 | 8 |  | Existing L.T line |  | 30 | 30 | 0 | 0 | 30 | 0 | 2.1 | 1 | 2.1 | 3 | 660 | 0 | 0 | 0 | 6 | 660
5 | Nayagarh | D | Ranpur | NAC | 3-9 | Nua rajabhati upersahi | 4 | Anganabadi Manikapatana | 20.070576,85.338595 | Ending point | 20.059333,85.341334 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
6 | Nayagarh | D | Ranpur | NAC | 9 | Way to Maninaga temple | 4 | Starting point | 20.060117,85.339524 | Ending point |  | 6000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 300 | 300 | 0 | 0 | 0 | 300 | 13.5 | 4 | 3.375 | 5 | 0 | 6600 | 0 | 0 | 60 | 6600
7 | Nayagarh | D | Ranpur | NAC | 9 | Maninaga to Hanuman temple | 4 | Maninaga temple | 20.060806,85.339543 | Ending point | 20.061712,85.338576 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
8 | Nayagarh | D | Ranpur | NAC | 12 | Lakhapada block road | 4.5 | Starting point | 20.052631,85.336024 | Ending point | 20.051056,85.332312 | 500 | M |  |  | Y |  | SS | 20 | 8 |  | Existing transformer |  | 25 | 25 | 0 | 0 | 25 | 0 | 1.75 | 1 | 1.75 | 3 | 550 | 0 | 0 | 0 | 5 | 550
9 | Nayagarh | D | Ranpur | NAC | 12 | Nuagaan village road | 4 | Starting point | 20.055463,85.339195 | Ending point | 20.054300,85.341032 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
10 | Nayagarh | D | Ranpur | NAC | 13 | Raghunathapur village road | 4 | Birabara Biswala house | 20.050556,85.340452 | Ending point | 20.050281,85.341788 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
11 | Nayagarh | D | Ranpur | NAC | 13-14 | Village road | 4.5 | Starting point | 20.047210,85.343726 | Nua Raghunathapur | 20.047359,85.348230 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
1 | Balangir | D | Titlagarh | Municipality | 9 | Dumping yard road | 5 | Desil village | 20.281789,83.172334 | Dumping yard | 20.269383,83.171929 | 1500 | M |  |  | Y |  | Ss | 20 | 8 |  | Existing L.T line |  | 75 | 75 | 0 | 0 | 75 | 0 | 5.25 | 1 | 5.25 | 7.5 | 0 | 0 | 1650 | 0 | 15 | 1650
2 | Balangir | D | Titlagarh | Municipality | 8 | NC nagar road | 3.5 | Starting point | 20.291221,83.160616 | Ending point | 20.288858,83.158927 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
3 | Balangir | D | Titlagarh | Municipality | 2 | Sargigada village road | 3 | Near NC nagar | 20.290518,83.161370 | Ending point | 20.286689,83.161278 | 850 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 43 | 43 | 0 | 0 | 0 | 43 | 1.935 | 1 | 1.935 | 3 | 935 | 0 | 0 | 0 | 9 | 935
4 | Balangir | D | Titlagarh | Municipality | 1 | Titidungri village road | 3.5 | Starting point | 20.304844,83.149207 | Ending point | 20.305680,83.150803 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
5 | Balangir | D | Titlagarh | Municipality | 1 | Titidungri village road | 3.5 | Sambalei mandira | 20.302291,83.149603 | RD road | 20.303696,83.152128 | 650 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 33 | 33 | 0 | 0 | 0 | 33 | 1.485 | 1 | 1.485 | 3 | 715 | 0 | 0 | 0 | 7 | 715
6 | Balangir | D | Titlagarh | Municipality | 1 | Nanajhar road | 4 | Jita Das house | 20.299016,83.152247 | Railway crossing | 20.309205,83.153621 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
7 | Balangir | D | Titlagarh | Municipality | 1 | Manigaan road | 4.5 | Woman collage | 20.303696,83.163442 | Ending point | 20.311982,83.161843 | 1200 | M |  |  | Y |  | Ss | 20 | 8 |  | Existing street light pole |  | 60 | 60 | 0 | 0 | 60 | 0 | 4.2 | 1 | 4.2 | 7.5 | 0 | 0 | 1320 | 0 | 12 | 1320
8 | Balangir | D | Titlagarh | Municipality | 1 | Silpada village road | 3.5 | Starting point | 20.306855,83.162015 | Ending point | 20.305269,83.160561 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
9 | Balangir | D | Titlagarh | Municipality | 13 | Debandhapada | 4 | Starting point | 20.282381,83.147993 | Ending point | 20.282815,83.148715 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
10 | Balangir | D | Titlagarh | Municipality | 13 | Siba mandira road | 3.5 | Starting point | 20.278709,83.147420 | Ending point | 20.276711,83.148854 | 650 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 33 | 33 | 0 | 0 | 0 | 33 | 1.485 | 1 | 1.485 | 3 | 715 | 0 | 0 | 0 | 7 | 715
11 | Balangir | D | Titlagarh | Municipality | 13 | Dhabaleswar school road | 4 | Fisari office | 20.280261,83.151360 | Dhabaleswar school | 20.282125,83.151412 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
12 | Balangir | D | Titlagarh | Municipality | 4-15 | Neherunagar | 4.5 | Starting point | 20.291266,83.145056 | Baidarpada | 20.290298,83.140841 | 1400 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 70 | 70 | 0 | 0 | 0 | 70 | 3.15 | 1 | 3.15 | 5 | 0 | 1540 | 0 | 0 | 14 | 1540
13 | Balangir | D | Titlagarh | Municipality | 15 | DAV collage road | 6 | DAV collage field | 20.283858,83.140639 | Indian petrol pump | 20.286356,83.143769 | 550 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 20 | 20 | 0 | 20 | 0 | 0 | 1.8 | 1 | 1.8 | 3 | 605 | 0 | 0 | 0 | 4 | 605
1 | Balangir | D | Tusura | NAC | 1 | Kharda village road | 4.5 | Smasan | 20.496927,83.484168 | Kharda school | 20.499315,83.484623 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
2 | Balangir | D | Tusura | NAC | 2-1 | Nagaon village road | 4 | Kharda harijanapada | 20.502597,83.482844 | Nagaon village | 20.500162,83.473301 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
3 | Balangir | D | Tusura | NAC | 1 | Nagaon basti road | 4 | Nagaon village | 20.503015,83.470670 | Nagaon basti | 20.504192,83.469154 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
4 | Balangir | D | Tusura | NAC | 1-8 | Mohepur Metagani village road | 4 | Nagaon school | 20.505268,83.466084 | Mohepur Metagani road | 20.497409,83.465963 | 900 | M |  |  | Y |  | SS | 20 | 8 |  | Existing L.T. line |  | 45 | 45 | 0 | 0 | 45 | 0 | 3.15 | 1 | 3.15 | 5 | 0 | 990 | 0 | 0 | 9 | 990
5 | Balangir | D | Tusura | NAC | 8 | Balangir main road | 7 | Starting point | 20.497456,83.463380 | Santosh rice mill | 20.500233,83.458516 | 600 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 22 | 22 | 0 | 22 | 0 | 0 | 1.98 | 1 | 1.98 | 3 | 660 | 0 | 0 | 0 | 4 | 660
6 | Balangir | D | Tusura | NAC | 8 | Mahipur village road | 3 | Uparpada | 20.493069,83.465041 | Ashram school | 20.494817,83.465220 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
7 | Balangir | D | Tusura | NAC | 8 | Burmar village road | 3.5 | Mahipur village | 20.490724,83.467393 | Burmar chhack | 20.484983,83.462735 | 1100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 55 | 55 | 0 | 0 | 0 | 55 | 2.475 | 1 | 2.475 | 5 | 0 | 1210 | 0 | 0 | 11 | 1210
8 | Balangir | D | Tusura | NAC | 8 | Burmar village road | 3.5 | PWD road | 20.833526,83.459515 | Pond | 20.484475,83.460040 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
9 | Balangir | D | Tusura | NAC | 7 | Dhangarh village road | 3 | Dhangarh main road | 20.484282,83.487507 | Ghantiapada | 20.484017,83.487119 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
10 | Balangir | D | Tusura | NAC | 11 | PWD to AWC road | 4 | PWD road | 21.484294,83.484792 | AWC chhack | 20.477328,83.492992 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
11 | Balangir | D | Tusura | NAC | 11 | Kapsila village road | 3.5 | Dhangarh | 20.475528,83.489278 | Kapsila chhack | 20.475879,83.483891 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T. line |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
12 | Balangir | D | Tusura | NAC | 9-10 | Kapsila road | 4 | Starting point | 20.471765,83.484480 | Siba mandira | 20.459895,83.481923 | 1400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T. line |  | 70 | 70 | 0 | 0 | 0 | 70 | 3.15 | 1 | 3.15 | 5 | 0 | 1540 | 0 | 0 | 14 | 1540
13 | Balangir | D | Tusura | NAC | 9 | Kapsila village road | 3.5 | Siba mandira | 20.457637,83.480116 | River | 20.457018,83.480275 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T. line |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
14 | Balangir | D | Tusura | NAC | 9 | Kapsila-Rugudipada road | 3.5 | Rugudipada chhack | 20.455127,83.471861 | Nuapada chari chhack | 20.457676,83.460290 | 2200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T. line |  | 110 | 110 | 0 | 0 | 0 | 110 | 4.95 | 1 | 4.95 | 7.5 | 0 | 0 | 2420 | 0 | 22 | 2420
15 | Balangir | D | Tusura | NAC | 10 | Janipada village road | 3 | Janipada chhack | 20.457491,93.477779 | Janipada | 20.466837,83.479434 | 1500 | M |  |  | Y |  | SS | 20 | 8 |  | Existing L.T. line |  | 75 | 75 | 0 | 0 | 75 | 0 | 5.25 | 1 | 5.25 | 7.5 | 0 | 0 | 1650 | 0 | 15 | 1650
1 | Nuapada | D | Khariar | NAC | 1 | Muktapur village road | 4 | Muktapur school | 20.310295,82.747691 | Kenal chhack | 20.311526,82.748584 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
2 | Nuapada | D | Khariar | NAC | 1 | Misan village road | 3.5 | Kenal road | 20.312488,82.743022 | Ending kenal road | 20.312320,82.751469 | 900 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 45 | 45 | 0 | 0 | 0 | 45 | 2.025 | 1 | 2.025 | 3 | 990 | 0 | 0 | 0 | 9 | 990
3 | Nuapada | D | Khariar | NAC | 1-2 | Main kenal road | 4.5 | Starting point | 20.318508,82.754523 | Sidhartha mohapatra road | 20.305127,82.754955 | 1500 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 75 | 75 | 0 | 0 | 75 | 0 | 5.25 | 1 | 5.25 | 7.5 | 0 | 0 | 1650 | 0 | 15 | 1650
4 | Nuapada | D | Khariar | NAC | 2 | Nayak chhack to training programme | 3 | Nayak chhack | 20.304364,82.756121 | Training programme office | 20.304368,82.757218 | 140 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 7 | 7 | 0 | 0 | 0 | 7 | 0.315 | 1 | 0.315 | 3 | 154 | 0 | 0 | 0 | 1 | 154
5 | Nuapada | D | Khariar | NAC | 2 | Santinagar village road | 3.5 | School chhack | 20.303378,82.758728 | Santinagar | 20.303858,82.757636 | 470 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 24 | 24 | 0 | 0 | 0 | 24 | 1.08 | 1 | 1.08 | 3 | 517 | 0 | 0 | 0 | 5 | 517
6 | Nuapada | D | Khariar | NAC | 2 | Bhojpur village | 4 | Sharma house | 20.299254,82.760283 | Kutipada chhack | 20.305838,82.762301 | 800 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 40 | 40 | 0 | 0 | 40 | 0 | 2.8 | 1 | 2.8 | 5 | 0 | 880 | 0 | 0 | 8 | 880
7 | Nuapada | D | Khariar | NAC | 4 | Balangir-Kantabanjhi road | 7 | Indian petrol pump | 20.295900,82.769509 | Durdharsan kenora | 20.296937,82.773300 | 400 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 15 | 15 | 0 | 15 | 0 | 0 | 1.35 | 1 | 1.35 | 3 | 440 | 0 | 0 | 0 | 3 | 440
8 | Nuapada | D | Khariar | NAC | 4 | Bhawanipatna main road | 7 | Pradhan complex | 20.287500,82.768105 | Indian petrol pump | 20.281978,82.772277 | 750 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 28 | 28 | 0 | 28 | 0 | 0 | 2.52 | 1 | 2.52 | 5 | 0 | 825 | 0 | 0 | 6 | 825
9 | Nuapada | D | Khariar | NAC | 12 | Siba mandira road | 3.5 | Main road | 20.283970,82.771171 | Siba mandira | 20.282914,82.768274 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
10 | Nuapada | D | Khariar | NAC | 11 | Sinapali road | 5 | Sinapali chhack | 20.272658,82.762427 | Phutupada | 20.269052,82.762442 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
11 | Nuapada | D | Khariar | NAC | 11 | Putopada village road | 4 | School chhack | 20.275013,82.759566 | Bijepur | 20.284232,82.752509 | 2000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 100 | 100 | 0 | 0 | 0 | 100 | 4.5 | 1 | 4.5 | 7.5 | 0 | 0 | 2200 | 0 | 20 | 2200
12 | Nuapada | D | Khariar | NAC | 13 | RMC godam road | 7 | Gandhi club | 20.284358,82.752265 | RMC godam | 20.287590,82.747796 | 600 | M |  |  | Y |  | SS | 27 | 9 |  | Existing street light pole |  | 22 | 22 | 0 | 0 | 22 | 0 | 1.54 | 1 | 1.54 | 3 | 660 | 0 | 0 | 0 | 4 | 660
13 | Nuapada | D | Khariar | NAC | 13 | Woman collage road | 4 | Ambedkar school | 20.284085,82.753075 | Woman collage | 20.289636,82.756529 | 1550 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 78 | 78 | 0 | 0 | 0 | 78 | 3.51 | 1 | 3.51 | 5 | 0 | 1705 | 0 | 0 | 16 | 1705
14 | Nuapada | D | Khariar | NAC | 8 | Lal house road | 4 | Vetnary chhack | 20.289545,82.756504 | Lal house | 20.289586.82.755000 | 550 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 605 | 0 | 0 | 0 | 6 | 605
15 | Nuapada | D | Khariar | NAC | 7 | Lalsapada village road | 4 | Bhajamana house | 20.294044,82.756502 | Sanju house | 20.295548,82.755679 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
1 | Bargarh | B | Bargarh | Municipality | 1 | Nigamananda ashram road | 3 | Starting point | 21.339953,83.608421 | Dinesh Biswal house | 21.338164,83.608330 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
2 | Bargarh | B | Bargarh | Municipality | 1-17 | Old NH-6 | 7 | Sai mandira | 21.341497,83.604883 | Circuit house | 21.333182,83.599782 | 2500 | M |  | Y |  |  | SS | 27 | 9 |  | Existing L.T. line | Road between a bridge | 93 | 93 | 0 | 93 | 0 | 0 | 8.37 | 2 | 4.185 | 7.5 | 0 | 0 | 2750 | 0 | 19 | 2750
3 | Bargarh | B | Bargarh | Municipality | 17 | Bargarh-Bijepur road | 7 | Banjari chhack | 21.323431,83.602180 | Banjari bridge | 21.320382,83.601815 | 300 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 11 | 11 | 0 | 11 | 0 | 0 | 0.99 | 1 | 0.99 | 3 | 330 | 0 | 0 | 0 | 2 | 330
4 | Bargarh | B | Bargarh | Municipality | 1-18 | NH-6 | 16 | Haldipali chhack | 21.338143,83.592168 | 16 No ward end | 21.348514,83.658397 | 5500 | 2W |  | Y |  |  | M | 27 | 9 |  | Existing street light pole | Center pole arrangement | 204 | 204 | 0 | 408 | 0 | 0 | 36.72 | 4 | 9.18 | 12 | 0 | 0 | 0 | 6050 | 41 | 6050
5 | Bargarh | B | Bargarh | Municipality | 16 | Kalinganagar village road | 7 | NH-6 | 21.348886,83.638553 | Ending point | 21.345929,83.634982 | 650 | M |  | Y |  |  | SS | 27 | 9 |  | Do |  | 24 | 24 | 0 | 24 | 0 | 0 | 2.16 | 1 | 2.16 | 3 | 715 | 0 | 0 | 0 | 5 | 715
6 | Bargarh | B | Bargarh | Municipality | 16 | Bramhachari road | 4 | Starting point | 21.354566,83.628385 | Kantapali | 21.358711,83.629697 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
7 | Bargarh | B | Bargarh | Municipality | 1 | Smasanghat road | 2.5 | Starting point | 21.332763,83.608430 | Jamuna bihar | 21.334937,83.606792 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
8 | Bargarh | B | Bargarh | Municipality | 16 | Leavel crossing to over bridge | 4 | Leavel crossing | 21.358254,83.629642 | Over bridge | 21.354881,83.635434 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
9 | Bargarh | B | Bargarh | Municipality | 19 | Malgodam road | 4 | Master tikira | 21.335789,83.636179 | Sharma babu house | 21.335880,83.638997 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
10 | Bargarh | B | Bargarh | Municipality | 19 | Reserve police chhack to Mishion hospital | 4.5 | Reserve police | 21.335842,83.632462 | Mishion hospital | 21.323837,83.645691 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
1 | Sonepur | D | Sonepur | Municipality | 2 | Tahasil Office to Excise Office | 4 | Tahasil Chhack | 20.844499,83.902039 | Excise Office | 20.8424561,83.899691 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
2 | Sonepur | D | Sonepur | Municipality | 2 | Excise Office Chhack | 4 | Excise Office Chhack | 20.842486,83.899726 | End Point | 20.844904,83.899341 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
3 | Sonepur | D | Sonepur | Municipality | 2 | Way to Balaji Abasika School | 4 | SH-41 | 20.845815,83.894124 | End Point | 20.844714,83.893277 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
4 | Sonepur | D | Sonepur | Municipality | 2 | Little Flower Chhack to Vigilance Office | 5.5 | Little Flower Chhack | 20.847257,83.889674 | Vigilance Office | 20.846068,83.887650 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
5 | Sonepur | D | Sonepur | Municipality | 2 | Gidco Point Back Side | 4 | Start Point | 20.843829,83.888601 | End Point | 20.844195,83.887459 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
6 | Sonepur | D | Sonepur | Municipality | 1 | Little Flower Chhack to Ramakrishna Nagar | 3.5 | Start Point | 20.847520,83.889698 | End Point | 20.848167,83.889315 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
7 | Sonepur | D | Sonepur | Municipality | 1 | Budharaja Chhack to Mattha Chhack | 13 | Budharaja Chhack | 20.852320,83.894862 | Mattha Chhack | 20.854152,83.889456 | 500 | M |  |  | Y |  | DS-Z-Z | 36 | 9 |  | Existing Street Light Pole |  | 28 | 28 | 0 | 0 | 28 | 0 | 1.96 | 1 | 1.96 | 3 | 1100 | 0 | 0 | 0 | 6 | 1100
8 | Sonepur | D | Sonepur | Municipality | 1 | Sambalpur to Sonepur Bridge | 9 | Start Point | 20.857497,83.897402 | Hekudi Chhack | 20.868560,83.908083 | 3600 | M |  |  | Y |  | DS-Z-Z | 36 | 9 |  | Existing Street Light Pole | 1.5 m footpath on both side | 200 | 200 | 0 | 0 | 200 | 0 | 14 | 2 | 7 | 12 | 0 | 0 | 0 | 7920 | 40 | 7920
9 | Sonepur | D | Sonepur | Municipality | 10 | Pattabhadi School Road | 9 | Pattabhadi School | 20.840179,83.895471 | End Point | 20.839280,83.892716 | 300 | M |  |  | Y |  | SS | 27 | 9 |  | Existing Highmast |  | 11 | 11 | 0 | 0 | 11 | 0 | 0.77 | 1 | 0.77 | 3 | 330 | 0 | 0 | 0 | 2 | 330
10 | Sonepur | D | Sonepur | Municipality | 12 | Telriver ring road | 7 | Bridge Point | 20.830140,83.908291 | Leprocy Colony | 20.835824,83.919268 | 1400 | M |  |  |  | Y | SS | 20 | 8 |  | No Transformer / SL Pole |  | 70 | 70 | 0 | 0 | 0 | 70 | 3.15 | 1 | 3.15 | 5 | 0 | 1540 | 0 | 0 | 14 | 1540
11 | Sonepur | D | Sonepur | Municipality | 12 | Subernmeru Temple | 4 | Subernmeru Temple | 20.833812,83.914817 | Ministadium Chhack | 20.837684,83.919406 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
12 | Sonepur | D | Sonepur | Municipality | 12-6 | Leprocy Colony to Rameshwara Temple | 7 | Leprocy Colony |  | Rameshwaram Temple | 20.838845,83.921223 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
13 | Sonepur | D | Sonepur | Municipality | 10 | Katalpada Chhack to Jailkhana | 5 | Katalpada Chhack | 20.845201,83.904521 | Jailkhana | 20.842970,83.903177 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT Pole |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
14 | Sonepur | D | Sonepur | Municipality | 10 | Katalpada Chhack to Nalinil Chhack | 7 | Start Point | 20.843119,83.906003 | Municipality Back road | 20.842261,83.908130 | 250 | M |  |  | Y |  | SS | 27 | 9 |  | Existing Transformer |  | 9 | 9 | 0 | 0 | 9 | 0 | 0.63 | 1 | 0.63 | 3 | 275 | 0 | 0 | 0 | 2 | 275
15 | Sonepur | D | Sonepur | Municipality | 12 | Nalinil Chhack to Sishu Udyan | 7 | Start Point | 20.841975,83.409045 | End Point | 20.840050,83.914003 | 550 | M |  |  | Y |  | SS | 27 | 9 |  | Existing Transformer |  | 20 | 20 | 0 | 0 | 20 | 0 | 1.4 | 1 | 1.4 | 3 | 605 | 0 | 0 | 0 | 4 | 605
16 | Sonepur | D | Sonepur | Municipality | 12 | Chammapuda to Fisher Office | 4 | Start Point | 20.841051,83.910708 | Fisher Office | 20.837774,83.907168 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
17 | Sonepur | D | Sonepur | Municipality | 10 | Talakulpada to Uperkulpada | 4 | Start Point | 20.837697,83.893804 | End Point | 20.835879,83.894103 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
18 | Sonepur | D | Sonepur | Municipality | 10 | Unmaned Village road | 4 | Start Point | 20.835885,83.894092 | Uperkulpada | 20.831636,83.893971 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
19 | Sonepur | D | Sonepur | Municipality | 10 | Uperkulpada Village to Bamdevjani House | 4 | Uperkulpada Village | 20.830489,83.894759 | Bamdevjani House | 20.828579,83.894979 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
20 | Sonepur | D | Sonepur | Municipality | 1 | SP Residance to Mahanadi Ring road | 4.5 | SP Residance | 20.852644,83.899365 | Mahanadi Ring road | 20.854386,83.900159 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
21 | Sonepur | D | Sonepur | Municipality | 1-5 | Mahanadi Ring road | 15 | Start Point | 20.856824,83.896882 | End Point |  | 2000 | M |  |  | Y |  | DS-Z-Z | 36 | 9 |  | Existing Street Light Pole |  | 112 | 112 | 0 | 0 | 112 | 0 | 7.84 | 1 | 7.84 | 12 | 0 | 0 | 0 | 4400 | 22 | 4400
1 | Kalahandi | E | Bhawanipatna | Municipality | 2 | Balaramnagar | 4 | Starting point | 19.919985,83.183803 | Ending point | 19.920421,83.183885 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
2 | Kalahandi | E | Bhawanipatna | Municipality | 2 | Kusadungri village road | 4 | RMC road | 19.916153,83.190949 | Ending point | 19.907214,83.188293 | 1400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 70 | 70 | 0 | 0 | 0 | 70 | 3.15 | 1 | 3.15 | 5 | 0 | 1540 | 0 | 0 | 14 | 1540
3 | Kalahandi | E | Bhawanipatna | Municipality | 15-16 | NH44 | 12 | Duarsuni chhack | 19.885267,83.161130 | Hill town | 19.896930,83.158125 | 1400 | M |  | Y |  |  | M | 27 | 9 |  | Existing street light | Center pole arrangement | 52 | 52 | 0 | 104 | 0 | 0 | 9.36 | 1 | 9.36 | 12 | 0 | 0 | 0 | 1540 | 10 | 1540
4 | Kalahandi | E | Bhawanipatna | Municipality | 1 | Hanuman temple to Radha Krushna temple | 4 | Hanuman temple | 19.904994,83.165625 | Radha Krushna temple | 19.905294,83.165058 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
5 | Kalahandi | E | Bhawanipatna | Municipality | 1 | Hanuman mandira to Santosi maa mandira | 4 | Hanuman mandira | 19.909007,83.175944 | Santosi maa mandira | 19.908969,83.175907 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
6 | Kalahandi | E | Bhawanipatna | Municipality | 1 | Choriharipada to Tarini mandira road | 4 | Choriharipada | 19.909873,83.176180 | Tarini mandira | 19.909796,83.176121 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
1 | Kandhamal | D | Baliguda | NAC | 2-1 | Bhagamunda to Kanpada Road | 4 | Bhagamunda Village | 20.207300,83.911613 | Ramesh Mallik House | 20.217663,83.913470 | 1300 | M |  |  | Y |  | SS | 20 | 8 |  | Existing Street Light Pole |  | 65 | 65 | 0 | 0 | 65 | 0 | 4.55 | 1 | 4.55 | 7.5 | 0 | 0 | 1430 | 0 | 13 | 1430
2 | Kandhamal | D | Baliguda | NAC | 1 | Kanpda to Badagaon Road | 4 | Kanpada | 20.219025,83.914892 | Rajni Bindhani House | 20.216440,83.918255 | 650 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 33 | 33 | 0 | 0 | 0 | 33 | 1.485 | 1 | 1.485 | 3 | 715 | 0 | 0 | 0 | 7 | 715
3 | Kandhamal | D | Baliguda | NAC | 1-2 | Anganbadi to Kattapadi Chhack | 4.5 | Badagaon Anganbadi | 20.216519,83.919691 | Rajeev Kahanra House | 20.209011,83.923400 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
4 | Kandhamal | D | Baliguda | NAC | 2 | Baliguda to Sindiri Gaon | 4.5 | Narsingh club | 20.209149,83.924238 | Ajit Mallik House | 20.212590,83.926299 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
5 | Kandhamal | D | Baliguda | NAC | 1 | Badagaon to Padasahi | 4.5 | Salaguda Sahi | 20.212148,83.925917 | Kattu Mallik | 20.213428,83.922416 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
6 | Kandhamal | D | Baliguda | NAC | 1 | Church Road | 4 | Rashadigal House | 20.215890,83.920746 | Badagaon UP school | 20.216229,83.923147 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
7 | Kandhamal | D | Baliguda | NAC | 2 | Dumudisahi School to PHD Office | 4.5 | Start Point | 20.203272,83.919407 | PHD Office | 20.202201,83.920200 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
8 | Kandhamal | D | Baliguda | NAC | 2 | Dumudisahi School to PHD Office | 4.5 | Gaurav Mallik House | 20.202659,83.919890 | Pradhan House | 20.202004,83.919029 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
9 | Kandhamal | D | Baliguda | NAC | 9 | Sub collector Resedential area to PWD Chhack | 4 | Sub collector Resedance | 20.199375,83.912462 | PWD Chhack | 20.199365,83.911568 | 120 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 6 | 6 | 0 | 0 | 0 | 6 | 0.27 | 1 | 0.27 | 3 | 132 | 0 | 0 | 0 | 1 | 132
10 | Kandhamal | D | Baliguda | NAC | 3 | Mundasahi RoaD | 5 | Start Point | 20.195050,83.918847 | Ravindra Digal House | 20.201054,83.923574 | 950 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 48 | 48 | 0 | 0 | 0 | 48 | 2.16 | 1 | 2.16 | 3 | 1045 | 0 | 0 | 0 | 10 | 1045
11 | Kandhamal | D | Baliguda | NAC | 3 | Bandapanga Road | 5 | Sudhanshu House | 20.202459,83.926094 | Bandapanga Primary School | 20.204604,83.928157 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
12 | Kandhamal | D | Baliguda | NAC | 2-3 | Bandapanga Primary School to Kattapadi Chhack | 4.5 | Bandapanga Primary School | 20.204646,83.928183 | Kattapadi Chhack | 20.208103,83.923527 | 700 | M |  |  | Y |  | SS | 20 | 8 |  | Existing Street Light Pole |  | 35 | 35 | 0 | 0 | 35 | 0 | 2.45 | 1 | 2.45 | 5 | 0 | 770 | 0 | 0 | 7 | 770
13 | Kandhamal | D | Baliguda | NAC | 2 | Sindirigaon Road | 4 | Radhakrishna Temple | 20.204733,83.920931 | End Point | 20.206557,83.922406 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
14 | Kandhamal | D | Baliguda | NAC | 4 | Nandapada Road | 4.5 | Start Point | 20.184015,83.929435 | Dhobaleshwar Mandir | 20.177762,83.929192 | 800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 40 | 40 | 0 | 0 | 0 | 40 | 1.8 | 1 | 1.8 | 3 | 880 | 0 | 0 | 0 | 8 | 880
15 | Kandhamal | D | Baliguda | NAC | 4 | Karnatakapur Village Road | 5 | Start Point | 20.181743,83.928342 | End Point | 20.181008,83.926730 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
16 | Kandhamal | D | Baliguda | NAC | 4 | Benaketa Village Road | 3.5 | Karnatakapur Chhack | 20.180245,83.926198 | Benaketa Village End | 20.177512,83.920975 | 750 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 38 | 38 | 0 | 0 | 0 | 38 | 1.71 | 1 | 1.71 | 3 | 825 | 0 | 0 | 0 | 8 | 825
17 | Kandhamal | D | Baliguda | NAC | 7 | Nuasahi Road | 4 | Naresh Nayak House | 20.187955,83.912549 | Jaranivasha | 20.184918,83.911979 | 450 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 23 | 23 | 0 | 0 | 0 | 23 | 1.035 | 1 | 1.035 | 3 | 495 | 0 | 0 | 0 | 5 | 495
18 | Kandhamal | D | Baliguda | NAC | 11-7 | Goliadanga Bypass | 4.5 | Panasapodi (New Renktipodi Girihanagar) |  | End Point | 20.203835,83.933381 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
19 | Kandhamal | D | Baliguda | NAC | 3 | Banghapanga | 4 | Banghapanga | 20.205197,83.930230 | Boda Nadi (Khadga) | 20.203835,83.933381 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole / Transformer at End |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
20 | Kandhamal | D | Baliguda | NAC | 11 | Girihanagar | 4.5 | Girihanagar | 20.188318,83.906850 | Jaranivasha | 20.184104,83.911223 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Mini Highmast |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
21 | Kandhamal | D | Baliguda | NAC | 7 | Sonasahi Road | 4 | Goibali Road | 20.171872,83.913819 | Surasahi | 20.169359,83.908492 | 700 | M |  |  | Y |  | SS | 20 | 8 |  | Existing Street Light Pole |  | 35 | 35 | 0 | 0 | 35 | 0 | 2.45 | 1 | 2.45 | 5 | 0 | 770 | 0 | 0 | 7 | 770
22 | Kandhamal | D | Baliguda | NAC | 7 | Nuvasahi Road to Iskipodi Chhack | 4 | Rangasuga House | 20.183197,83.912573 | Nischal Nayak House | 20.164725,83.913191 | 2200 | M |  |  | Y |  | SS | 20 | 8 |  | Existing Street Light Pole |  | 110 | 110 | 0 | 0 | 110 | 0 | 7.7 | 1 | 7.7 | 12 | 0 | 0 | 0 | 2420 | 22 | 2420
1 | Kandhamal | D | G.Udaygiri | NAC | 1 | Bellaguntha to Baragaon | 7.5 | Padasahi | 20.137420,84.378445 | End Point |  | 900 | M |  | Y |  |  | SS | 27 | 9 |  | Existing Street Light Pole |  | 33 | 33 | 0 | 33 | 0 | 0 | 2.97 | 1 | 2.97 | 5 | 0 | 990 | 0 | 0 | 7 | 990
2 | Kandhamal | D | G.Udaygiri | NAC | 1 | Pukulinga Road | 4 | Surendra kota House | 20.138976,84.371003 | Pukulinga Pond | 20.140603,84.370616 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
3 | Kandhamal | D | G.Udaygiri | NAC | 1 | Ajaypada Road | 4 | Duggudi Hostel | 20.129791,84.375200 | End Point | 20.127436,84.377101 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
4 | Kandhamal | D | G.Udaygiri | NAC | 3 | Siba temple Road | 4 | Maa Bearaleni Supply | 20.125492,84.366085 | Siba Temple | 20.126631,84.366375 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
5 | Kandhamal | D | G.Udaygiri | NAC | 4 | Sreeram Pada Sahi | 4 | Tanuj Nayak House | 20.125138,84.364032 | End Point | 20.122492,84.362604 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
6 | Kandhamal | D | G.Udaygiri | NAC | 4 | Indira Filed Road | 4 | Jail Quarter | 20.128852,84.360526 | Brahmapradhan House | 20.129232,84.357439 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
7 | Kandhamal | D | G.Udaygiri | NAC | 4 | Samanuita Office Road | 4 | Samanuita Office | 20.128169,84.358544 |  | 20.126762,84.357388 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
8 | Kandhamal | D | G.Udaygiri | NAC | 4 | Kalinga Mahavidyalay | 5 | Fiore Station G Udaygiri | 20.130710,84.359712 | End Point | 20.133201,84.356618 | 450 | M |  |  | Y |  | SS | 20 | 8 |  | Existing Street Light Pole |  | 23 | 23 | 0 | 0 | 23 | 0 | 1.61 | 1 | 1.61 | 3 | 495 | 0 | 0 | 0 | 5 | 495
9 | Kandhamal | D | G.Udaygiri | NAC | 13 | Balupanga Road | 4 | Balupanga Village | 20.104964,84.358380 | End Point | 20.104269,84.357752 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Village Transformer |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
10 | Kandhamal | D | G.Udaygiri | NAC | 13 | Balusuga Road | 4 | Starting Point | 20.114814,84.366972 | Bulusuga Village | 20.114685,84.363519 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Village Transformer |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
11 | Kandhamal | D | G.Udaygiri | NAC | 12 | Bellaguntha to Baragaon (MMC Road) | 7.5 | MMC High School | 20.112166,84.367951 | Pump House | 20.108889,84.368249 | 350 | M |  | Y |  |  | SS | 27 | 9 |  | Existing Transformer |  | 13 | 13 | 0 | 13 | 0 | 0 | 1.17 | 1 | 1.17 | 3 | 385 | 0 | 0 | 0 | 3 | 385
12 | Kandhamal | D | G.Udaygiri | NAC | 12 | Dam Road | 4 | Starting Point | 20.105538,84.372313 | End Point | 20.104186,84.373500 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
13 | Kandhamal | D | G.Udaygiri | NAC | 12 | Parashanagu Village | 4 | Starting Point | 20.119452,84.371309 | End Point | 20.105292,84.372329 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
14 | Kandhamal | D | G.Udaygiri | NAC | 11 | Newcourt Building | 4 | Starting Point | 20.119452,84.371309 | End Point | 20.118691,84.372276 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
15 | Kandhamal | D | G.Udaygiri | NAC | 11 | Hathibali Road | 4 | Hathibali Temple | 20.114899,84.373269 | End Point | 20.110919,84.379066 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
16 | Kandhamal | D | G.Udaygiri | NAC | 11 | Hathibali Sahi Road | 4 | Government Girls High School | 20.118743,84.375620 | Hathibali Sahi Village | 20.117596,84.374816 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Street Light Pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
1 | Raygada | E | Raygada | Municipality | 1 | Ramachandrapur village road | 3 | MG temple bridge | 19.154016,83.408366 | Ramchandrapur village | 19.149214,83.415936 | 1300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 65 | 65 | 0 | 0 | 0 | 65 | 2.925 | 1 | 2.925 | 5 | 0 | 1430 | 0 | 0 | 13 | 1430
2 | Raygada | E | Raygada | Municipality | 1 | MG temple road | 3 | MG temple | 19.153417,83.409137 | Link road | 19.160261,83.412924 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
3 | Raygada | E | Raygada | Municipality | 9 | Ramachandrapur village road | 3 | DFO 5th road | 19.159200,83.414536 | Ramchandrapur village | 19.148750,83.417209 | 2500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 125 | 125 | 0 | 0 | 0 | 125 | 5.625 | 2 | 2.8125 | 5 | 0 | 2750 | 0 | 0 | 25 | 2750
4 | Raygada | E | Raygada | Municipality | 1 | Gurumguda village road | 2.5 | Gurumguda | 19.142093,83.424507 | DFO office | 19.154957,83.420725 | 2700 | M |  |  |  | Y | SS | 20 | 8 |  | Do |  | 135 | 135 | 0 | 0 | 0 | 135 | 6.075 | 2 | 3.0375 | 5 | 0 | 2970 | 0 | 0 | 27 | 2970
5 | Raygada | E | Raygada | Municipality | 14 | Chekaguda road | 3.5 | Bridge | 19.170724,83.430685 | Chekaguda | 19.169767,83.428072 | 400 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 20 | 20 | 0 | 0 | 20 | 0 | 1.4 | 1 | 1.4 | 3 | 440 | 0 | 0 | 0 | 4 | 440
6 | Raygada | E | Raygada | Municipality | 14 | Prempahacla | 3 | Starting point | 19.170393,83.423853 | Ending point | 19.169379,83.424452 | 800 | M |  |  | Y |  | SS | 20 | 8 |  | Do |  | 40 | 40 | 0 | 0 | 40 | 0 | 2.8 | 1 | 2.8 | 5 | 0 | 880 | 0 | 0 | 8 | 880
7 | Raygada | E | Raygada | Municipality | 19 | Tumbhiguda village road | 3 | Kandha tumbhiguda chhack | 19.182724,83.424296 | Tumbhiguda chhack | 19.184154,83.422888 | 210 | M |  |  | Y |  | SS | 20 | 8 |  | Do |  | 11 | 11 | 0 | 0 | 11 | 0 | 0.77 | 1 | 0.77 | 3 | 231 | 0 | 0 | 0 | 2 | 231
1 | Koraput | E | Koraput | Municipality | 15 | Gunthaguda village road | 3.5 | Smasan | 18.829194,82.715610 | Gunthaguda village | 18.835614,82.720942 | 2500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 125 | 125 | 0 | 0 | 0 | 125 | 5.625 | 2 | 2.8125 | 5 | 0 | 2750 | 0 | 0 | 25 | 2750
2 | Koraput | E | Koraput | Municipality | 15 | Gunthaguda village road | 3 | Railway crossing | 18.822568,82.716680 | Gunthaguda village | 18.827155,82.717723 | 550 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 605 | 0 | 0 | 0 | 6 | 605
3 | Koraput | E | Koraput | Municipality | 15 | NH road Dengaguda | 3-7 | Bada chindri | 18.816076,82.730974 | Dengaguda village | 18.818176,82.751304 | 3400 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole | NH with Village road | 126 | 126 | 0 | 126 | 0 | 0 | 11.34 | 2 | 5.67 | 7.5 | 0 | 0 | 3740 | 0 | 25 | 3740
4 | Koraput | E | Koraput | Municipality | 16 | Tentuliguda village road | 3 | Dengaguda bridge | 18.819376,82.752119 | Tentuliguda village | 18.826452,82.754001 | 1700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 85 | 85 | 0 | 0 | 0 | 85 | 3.825 | 1 | 3.825 | 5 | 0 | 1870 | 0 | 0 | 17 | 1870
5 | Koraput | E | Koraput | Municipality | 15 | Akashguda village road | 3 | Bada kendri chhack | 18.817669,82.731332 | Akashguda village | 18.825875,82.732343 | 1500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 75 | 75 | 0 | 0 | 0 | 75 | 3.375 | 1 | 3.375 | 5 | 0 | 1650 | 0 | 0 | 15 | 1650
6 | Koraput | E | Koraput | Municipality | 16 | Chindri Maliguda village road | 3 | Sana chindri chhack | 18.815078,82.723490 | Chindri maliguda chhack | 18.811827,82.743457 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
7 | Koraput | E | Koraput | Municipality | 20 | Pokiaguda village road | 3 | OMP chhack | 18.790195,82.729775 | Pokiaguda chhack | 18.791350,82.743929 | 1700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 85 | 85 | 0 | 0 | 0 | 85 | 3.825 | 1 | 3.825 | 5 | 0 | 1870 | 0 | 0 | 17 | 1870
8 | Koraput | E | Koraput | Municipality | 20 | Jhatiguda village road | 3 | Siba mandira | 18.786225,82.729168 | Jhatiguda chhack | 18.778698,82.724919 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
9 | Koraput | E | Koraput | Municipality | 19 | Dengadeula village road | 3.5 | Railway station | 18.784395,82.720656 | Dengaguda village | 18.774254,82.720708 | 1300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 65 | 65 | 0 | 0 | 0 | 65 | 2.925 | 1 | 2.925 | 5 | 0 | 1430 | 0 | 0 | 13 | 1430
10 | Koraput | E | Koraput | Municipality | 6 | NH 26 | 7 | Ambedkar collage | 18.815331,82.697364 | Petrol pump | 18.816228,82.694112 | 350 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 13 | 13 | 0 | 13 | 0 | 0 | 1.17 | 1 | 1.17 | 3 | 385 | 0 | 0 | 0 | 3 | 385
11 | Koraput | E | Koraput | Municipality | 17 | Rangaballikumbha village road | 4 | Sobha office | 18.810943,82.697773 | Rangaballikumbha village | 18.766323,82.680500 | 3700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 185 | 185 | 0 | 0 | 0 | 185 | 8.325 | 2 | 4.1625 | 7.5 | 0 | 0 | 4070 | 0 | 37 | 4070
1 | Koraput | E | Kotpad | NAC | 12 | Mangalisahi village road | 4 | New bus stand | 19.139437,82.317147 | Mangali sahi | 19.138853,82.320371 | 350 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 18 | 18 | 0 | 0 | 18 | 0 | 1.26 | 1 | 1.26 | 3 | 385 | 0 | 0 | 0 | 4 | 385
2 | Koraput | E | Kotpad | NAC | 1 | Grila road | 6 | Grila road | 19.142793,82.336127 | Nuaguda | 19.145843,82.341782 | 400 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 20 | 20 | 0 | 0 | 20 | 0 | 1.4 | 1 | 1.4 | 3 | 440 | 0 | 0 | 0 | 4 | 440
3 | Koraput | E | Kotpad | NAC | 1 | Kunjaguda village road | 3 | Starting point | 19.142652,82.333192 | Basuli Nuaguda | 19.146236,82.332360 | 750 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 38 | 38 | 0 | 0 | 0 | 38 | 1.71 | 1 | 1.71 | 3 | 825 | 0 | 0 | 0 | 8 | 825
4 | Koraput | E | Kotpad | NAC | 1 | Collage road | 3.5 | Collage gate | 19.140566,82.356776 | Ending point | 19.138721,82.336129 | 200 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 10 | 10 | 0 | 0 | 10 | 0 | 0.7 | 1 | 0.7 | 3 | 220 | 0 | 0 | 0 | 2 | 220
5 | Koraput | E | Kotpad | NAC | 1 | NH 63 | 7 | NH SSD school | 19.133156,82.343150 | Bramhaneedei temple | 19.134825,82.350098 | 800 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 30 | 30 | 0 | 30 | 0 | 0 | 2.7 | 1 | 2.7 | 5 | 0 | 880 | 0 | 0 | 6 | 880
6 | Koraput | E | Kotpad | NAC | 1 | Kendugada village road | 4.5 | Telicome exchange office | 19.134726,82.330431 | English medium school | 19.129764,82.330608 | 850 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 43 | 43 | 0 | 0 | 43 | 0 | 3.01 | 1 | 3.01 | 5 | 0 | 935 | 0 | 0 | 9 | 935
7 | Koraput | E | Kotpad | NAC | 13 | Kusuli village road | 4 | Mandira chhack | 19.129884,82.320925 | Gas factory chhack | 19.121940,82.319282 | 900 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 45 | 45 | 0 | 0 | 45 | 0 | 3.15 | 1 | 3.15 | 5 | 0 | 990 | 0 | 0 | 9 | 990
8 | Koraput | E | Kotpad | NAC | 13 | Gandaguda road | 4 | Starting point | 19.130902,82.313627 | Narsimha temple | 19.127973,82.312187 | 350 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 18 | 18 | 0 | 0 | 18 | 0 | 1.26 | 1 | 1.26 | 3 | 385 | 0 | 0 | 0 | 4 | 385
9 | Koraput | E | Kotpad | NAC | 12 | Sub jail road | 4 | Kela rice mill | 19.138491,82.312220 | Jail road end | 19.135735,82.313369 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
1 | Nabrangpur | E | Umarkote | Municipality | 1 | Tuperbeda village road | 3 | Durgaguda | 19.694227,82.198468 | Tuperbeda | 19.695276,82.198600 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
2 | Nabrangpur | E | Umarkote | Municipality | 1-6 | Nuaguda village road | 3 | Durgaguda | 19.693684,82.199501 | Nuaguda | 19.668754,82.203104 | 1400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 70 | 70 | 0 | 0 | 0 | 70 | 3.15 | 1 | 3.15 | 5 | 0 | 1540 | 0 | 0 | 14 | 1540
3 | Nabrangpur | E | Umarkote | Municipality | 6-1 | Rajamunda village road | 3 | Rajamunda | 19.689634,82.211735 | Petrol pump | 19.671549,82.201437 | 1500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 75 | 75 | 0 | 0 | 0 | 75 | 3.375 | 1 | 3.375 | 5 | 0 | 1650 | 0 | 0 | 15 | 1650
4 | Nabrangpur | E | Umarkote | Municipality | 14-11 | Chadheiguda village road | 3.5 | Medical chhack | 19.653833,82.201890 | Chadheiguda chhack | 19.649926,82.209207 | 1100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 55 | 55 | 0 | 0 | 0 | 55 | 2.475 | 1 | 2.475 | 5 | 0 | 1210 | 0 | 0 | 11 | 1210
5 | Nabrangpur | E | Umarkote | Municipality | 11-14 | Bhagabatinagar village road | 3.5 | Siba mandira | 19.646641,82.201317 | Medical chhack | 19.657023,82.208671 | 1800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 90 | 90 | 0 | 0 | 0 | 90 | 4.05 | 1 | 4.05 | 7.5 | 0 | 0 | 1980 | 0 | 18 | 1980
6 | Nabrangpur | E | Umarkote | Municipality | 13 | Ektaguda village road | 4 | Ektaguda chhack | 19.659972,82.224221 | Ektaguda village | 19.661674,82.226392 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
7 | Nabrangpur | E | Umarkote | Municipality | 12 | NH | 7 | Dungriguda | 19.656432,82.219644 | Dharmakanta chhack | 19.646446,82.233037 | 700 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 26 | 26 | 0 | 26 | 0 | 0 | 2.34 | 1 | 2.34 | 3 | 770 | 0 | 0 | 0 | 5 | 770
8 | Nabrangpur | E | Umarkote | Municipality | 7 | Nuaguda A/C road | 5 | Mile stone | 19.669249,82.214513 | Nuaguda A/C chhack | 19.674630,82.216834 | 900 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 45 | 45 | 0 | 0 | 45 | 0 | 3.15 | 1 | 3.15 | 5 | 0 | 990 | 0 | 0 | 9 | 990
9 | Nabrangpur | E | Umarkote | Municipality | 8 | Kenal sahi village | 3 | Starting point | 19.660343,82.203943 | Bandha chhack | 19.656486,82.197120 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
10 | Nabrangpur | E | Umarkote | Municipality | 8 | Dangrisahi village road | 3 | Bandhahuda | 19.668764,82.197248 | Dangrisahi | 19.668282,82.194185 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
11 | Nabrangpur | E | Umarkote | Municipality | 2 | Gatiguda village road | 4 | Starting point | 19.666755,82.187026 | Bridge | 19.667513,82.190729 | 200 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 10 | 10 | 0 | 0 | 10 | 0 | 0.7 | 1 | 0.7 | 3 | 220 | 0 | 0 | 0 | 2 | 220
12 | Nabrangpur | E | Umarkote | Municipality | 2 | Gatiguda village road | 3.5 | Bandha chhack | 19.670623,82.190531 | Ending point | 19.671020,82.187680 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
1 | Sambalpur | B | Sambalpur | M. Corporation | 36 | Khandual village road | 4 | NH | 21.420962,83.989705 | Ending point | 21.421127,83.994966 | 550 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 605 | 0 | 0 | 0 | 6 | 605
2 | Sambalpur | B | Sambalpur | M. Corporation | 36 | Anlaapali village road | 3.5 | Khandual road | 21.427309,84.004211 | Anlaapali | 21.436767,84.004265 | 900 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 45 | 45 | 0 | 0 | 0 | 45 | 2.025 | 1 | 2.025 | 3 | 990 | 0 | 0 | 0 | 9 | 990
3 | Sambalpur | B | Sambalpur | M. Corporation | 38 | Khairapali village road | 3.5 | NH | 21.436930,84.004543 | Khairapali | 21.440283,84.019782 | 2200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 110 | 110 | 0 | 0 | 0 | 110 | 4.95 | 1 | 4.95 | 7.5 | 0 | 0 | 2420 | 0 | 22 | 2420
4 | Sambalpur | B | Sambalpur | M. Corporation | 40 | Manasar village road | 4 | Khairapali village | 21.432912,84.019554 | Ending point | 21.430044,84.020067 | 300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 15 | 15 | 0 | 0 | 0 | 15 | 0.675 | 1 | 0.675 | 3 | 330 | 0 | 0 | 0 | 3 | 330
5 | Sambalpur | B | Sambalpur | M. Corporation | 38 | Paramanupur road | 6 | Sindurpank chhack | 21.452551,84.027654 | Dhandeipali chhack | 21.456952,84.031602 | 650 | M |  | Y |  |  | M | 27 | 9 |  | Existing street light pole | Center pole arrangement | 24 | 24 | 0 | 48 | 0 | 0 | 4.32 | 1 | 4.32 | 7.5 | 0 | 0 | 715 | 0 | 5 | 715
6 | Sambalpur | B | Sambalpur | M. Corporation | 38 | Paramanupur road | 6 | Dandeipali chhack | 21.456952,84.031602 | Themra chhack | 21.466406,84.042498 | 2700 | M |  | Y |  |  | M | 27 | 9 |  | Existing street light pole | Center pole arrangement | 100 | 100 | 0 | 200 | 0 | 0 | 18 | 2 | 9 | 12 | 0 | 0 | 0 | 2970 | 20 | 2970
7 | Sambalpur | B | Sambalpur | M. Corporation | 39 | Themra village road | 4 | Themra hospital | 21.471538,84.043005 | Ending point | 21.475926,84.042892 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
8 | Sambalpur | B | Sambalpur | M. Corporation | 39 | Themra to NH | 4 | Starting point | 21.476906,84.045761 | NH | 21.474832,84.051269 | 650 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 33 | 33 | 0 | 0 | 0 | 33 | 1.485 | 1 | 1.485 | 3 | 715 | 0 | 0 | 0 | 7 | 715
9 | Sambalpur | B | Sambalpur | M. Corporation | 39 | Themra village road | 4 | High school | 21.480863,84.031519 | Jhankarpada | 21.478232,84.008121 | 2600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 130 | 130 | 0 | 0 | 0 | 130 | 5.85 | 2 | 2.925 | 5 | 0 | 2860 | 0 | 0 | 26 | 2860
10 | Sambalpur | B | Sambalpur | M. Corporation | 41 | Dhamma road | 9 | Bhatra chhack | 21.432064,83.990255 | Gundarpur petrol pump | 21.409179,83.988881 | 2600 | M |  | Y |  |  | SS | 27 | 9 |  | Existing transformer |  | 96 | 96 | 0 | 96 | 0 | 0 | 8.64 | 2 | 4.32 | 7.5 | 0 | 0 | 2860 | 0 | 19 | 2860
11 | Sambalpur | B | Sambalpur | M. Corporation | 41 | Gundarpur Chhack – Chhatabara Village | 9-4 | Gundarpur chhack | 21.402416,83.987406 | Chhatabara ending point | 21.389758,83.991863 | 2100 | M |  | Y |  |  | SS | 27 | 9 |  | Existing L.T line | NH with village road | 78 | 78 | 0 | 78 | 0 | 0 | 7.02 | 1 | 7.02 | 12 | 0 | 0 | 0 | 2310 | 16 | 2310
12 | Sambalpur | B | Sambalpur | M. Corporation | 41 | Dhamma road | 9 | Starting point | 21.403477,83.987819 | Sarkipali village road | 21.409558,84.005341 | 2100 | M |  |  | Y |  | SS | 27 | 9 |  | Existing street light pole |  | 78 | 78 | 0 | 0 | 78 | 0 | 5.46 | 1 | 5.46 | 7.5 | 0 | 0 | 2310 | 0 | 16 | 2310
13 | Sambalpur | B | Sambalpur | M. Corporation | 41 | Sarkipalli Village Road | 4 | Starting point | 21.409411,84.005105 | Ending point | 21.403079,84.008170 | 850 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 43 | 43 | 0 | 0 | 0 | 43 | 1.935 | 1 | 1.935 | 3 | 935 | 0 | 0 | 0 | 9 | 935
14 | Sambalpur | B | Sambalpur | M. Corporation | 41 | Gulunda – Maneswar Market | 4 | Gulunda | 21.409524,84.005508 | Maneswar market | 21.412728,84.029904 | 2700 | M |  |  | Y |  | SS | 20 | 8 |  | Existing L.T line |  | 135 | 135 | 0 | 0 | 135 | 0 | 9.45 | 2 | 4.725 | 7.5 | 0 | 0 | 2970 | 0 | 27 | 2970
15 | Sambalpur | B | Sambalpur | M. Corporation | 40 | ITI Chhack- Sudunga | 4 | ITI chhack | 21.422690,84.038240 | Sudunga village | 21.412183,84.058550 | 2400 | M |  |  | Y |  | SS | 20 | 8 |  | Existing L.T line |  | 120 | 120 | 0 | 0 | 120 | 0 | 8.4 | 2 | 4.2 | 7.5 | 0 | 0 | 2640 | 0 | 24 | 2640
16 | Sambalpur | B | Sambalpur | M. Corporation | 40 | Meregmuda- Rasanpur | 2.5 | Mergamuda | 21.426455,84.041187 | Rasanpur | 21.431148,84.052528 | 7800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 390 | 390 | 0 | 0 | 0 | 390 | 17.55 | 5 | 3.51 | 5 | 0 | 8580 | 0 | 0 | 78 | 8580
17 | Sambalpur | B | Sambalpur | M. Corporation | 40 | Talpali Village -Sapali Village | 3.5 | Talpali village road | 21.427503,84.059911 | Salpali village road | 21.420336,84.057031 | 3700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 185 | 185 | 0 | 0 | 0 | 185 | 8.325 | 2 | 4.1625 | 7.5 | 0 | 0 | 4070 | 0 | 37 | 4070
18 | Sambalpur | B | Sambalpur | M. Corporation | 40 | Way to Kalpali Bridge | 4 | Starting point | 21.429676,84.066392 | Kalpali Bridge | 21.434669,84.067379 | 600 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 22 | 22 | 0 | 22 | 0 | 0 | 1.98 | 1 | 1.98 | 3 | 660 | 0 | 0 | 0 | 4 | 660
19 | Sambalpur | B | Sambalpur | M. Corporation | 39 | Talpali Village -vhopali Village | 9-5 | Talpali village road | 21.430282,84.062499 | Vhoipali | 21.428836,84.070227 | 800 | M |  |  | Y |  | SS | 27 | 9 |  | Existing street light pole | NH with village road | 30 | 30 | 0 | 0 | 30 | 0 | 2.1 | 1 | 2.1 | 3 | 880 | 0 | 0 | 0 | 6 | 880
20 | Sambalpur | B | Sambalpur | M. Corporation | 28 | Sambalpur Science Collage – Sankarama | 3 | Sambalpur Science Collage | 21.482895,84.000645 | Sankarma | 21.493205,84.006127 | 1800 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 90 | 90 | 0 | 0 | 0 | 90 | 4.05 | 1 | 4.05 | 7.5 | 0 | 0 | 1980 | 0 | 18 | 1980
21 | Sambalpur | B | Sambalpur | M. Corporation | 20 | Singhpali – Kainsir | 5 | Singhpali (Mahaveer Chhack) | 21.507516,83.904827 | Jogipali Village | 21.529478,83.982237 | 2300 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 115 | 115 | 0 | 0 | 0 | 115 | 5.175 | 2 | 2.5875 | 5 | 0 | 2530 | 0 | 0 | 23 | 2530
22 | Sambalpur | B | Sambalpur | M. Corporation | 20 | Kainsir Road | 3.5 | Starting point | 21.528514,83.983397 | Ending point | 21.526601,83.983968 | 2200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 110 | 110 | 0 | 0 | 0 | 110 | 4.95 | 1 | 4.95 | 7.5 | 0 | 0 | 2420 | 0 | 22 | 2420
23 | Sambalpur | B | Sambalpur | M. Corporation | 20-13 | Baraipali – Densergi | 3.5 | Baraipali | 21.498034,83.964070 | Densergi | 21.505388,83.965733 | 750 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 38 | 38 | 0 | 0 | 0 | 38 | 1.71 | 1 | 1.71 | 3 | 825 | 0 | 0 | 0 | 8 | 825
24 | Sambalpur | B | Sambalpur | M. Corporation | 13 | Juanpali Village Road | 4 | Junapali | 21.501672,83.960288 | Barinipali Police Station | 21.497303,83.961351 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
25 | Sambalpur | B | Sambalpur | M. Corporation | 13 | Gopalpali Village Road | 4 | Gopalpali | 21.500477,83.951446 | Ending point | 21.504053,83.953589 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
26 | Sambalpur | B | Sambalpur | M. Corporation | 8 | Nimpali Village Road | 4 | Starting point | 21.523401,83.904964 | Ending point | 21.520074,83.904311 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existingt Transformer |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
27 | Sambalpur | B | Sambalpur | M. Corporation | 13 | Sabalhar village road | 4 | Starting point | 21.504071,83.941002 | Ending point | 21.513753,83.949195 | 2000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 100 | 100 | 0 | 0 | 0 | 100 | 4.5 | 1 | 4.5 | 7.5 | 0 | 0 | 2200 | 0 | 20 | 2200
28 | Sambalpur | B | Sambalpur | M. Corporation | 13 | Sabalhar to Gopalpali | 4 | Starting point | 21.513753,83.949195 | Ending point | 21.506192,83.954389 | 1200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 60 | 60 | 0 | 0 | 0 | 60 | 2.7 | 1 | 2.7 | 5 | 0 | 1320 | 0 | 0 | 12 | 1320
29 | Sambalpur | B | Sambalpur | M. Corporation | 14,15,16 | Ring road Durgapali to Court chhack | 10 | Starting point | 21.498853,83.931273 | Court Chhack | 21.482906,83.946762 | 4500 | M |  | Y |  |  | SS | 27 | 9 |  | Existing street light pole |  | 167 | 167 | 0 | 167 | 0 | 0 | 15.03 | 3 | 5.01 | 7.5 | 0 | 0 | 4950 | 0 | 33 | 4950
30 | Sambalpur | B | Sambalpur | M. Corporation | 7 | New colony | 4 | Starting point | 21.506333,83.889578 | Ending point | 21.508733,83.889400 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
31 | Sambalpur | B | Sambalpur | M. Corporation | 7 | Sourav Bihar | 4.5 | Starting point | 21.498701,83.894927 | Ending point | 21.500170,83.894674 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
32 | Sambalpur | B | Sambalpur | M. Corporation | 7 | Kirba road | 3.5 | Starting point | 21.505518,83.903613 | River side | 21.506630,83.904497 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
33 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Power channel road | 4 | Railway crossing | 21.493790,83.913887 | Mudoghat bridge | 21.457363,83.946804 | 5000 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 250 | 250 | 0 | 0 | 250 | 0 | 17.5 | 3 | 5.8333 | 7.5 | 0 | 0 | 5500 | 0 | 50 | 5500
34 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Gosala road | 6 | Mudoghat chhack | 21.456740,83.946161 | Jharapali village road | 21.445928,83.943399 | 1300 | M |  |  | Y |  | SS | 20 | 8 |  | Existing transformer |  | 65 | 65 | 0 | 0 | 65 | 0 | 4.55 | 1 | 4.55 | 7.5 | 0 | 0 | 1430 | 0 | 13 | 1430
35 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Potapali village road | 5 | Mudoghat chhack | 21.457449,83.94661 | Potapali village | 21.468011,83.933372 | 2000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 100 | 100 | 0 | 0 | 0 | 100 | 4.5 | 1 | 4.5 | 7.5 | 0 | 0 | 2200 | 0 | 20 | 2200
36 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Thanapada village road | 3.5 | Starting point | 21.464284,83.946301 | Mudoghat village | 21.462166,83.951435 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
37 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Barhakuni village road | 4 | Mudoghat bridge | 21.457136,83.947020 | Barhakuni village | 21.450531,83.954289 | 1500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 75 | 75 | 0 | 0 | 0 | 75 | 3.375 | 1 | 3.375 | 5 | 0 | 1650 | 0 | 0 | 15 | 1650
38 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Chaunpur village road | 4.5 | Barhakuni chhack | 21.448627,83.952074 | Chhaunpur village | 21.440501,83.969707 | 2700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 135 | 135 | 0 | 0 | 0 | 135 | 6.075 | 2 | 3.0375 | 5 | 0 | 2970 | 0 | 0 | 27 | 2970
39 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Chaunpur main road | 4.5 | Chuanpur school | 21.432394,83.968500 | New Jharapali road | 21.440822,83.953861 | 1850 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 93 | 93 | 0 | 0 | 0 | 93 | 4.185 | 1 | 4.185 | 7.5 | 0 | 0 | 2035 | 0 | 19 | 2035
40 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Ghanteswar temple road | 4.5 | Jharapali chhack | 21.433268,83.963359 | Tihikipali village | 21.372857,83.940927 | 8200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 410 | 410 | 0 | 0 | 0 | 410 | 18.45 | 5 | 3.69 | 5 | 0 | 9020 | 0 | 0 | 82 | 9020
41 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Ghanteswar temple road | 4.5 | Tihikipali chhack | 21.384038,83.939146 | Ghanteswar temple | 21.354911,83.963342 | 4100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 205 | 205 | 0 | 0 | 0 | 205 | 9.225 | 3 | 3.075 | 5 | 0 | 4510 | 0 | 0 | 41 | 4510
42 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Badsinghari road | 4 | Badsinghari village road | 21.416050,83.930805 | Badsinghari village | 21.420716,83.934789 | 700 | M |  |  | Y |  | SS | 20 | 8 |  | Existing transformer |  | 35 | 35 | 0 | 0 | 35 | 0 | 2.45 | 1 | 2.45 | 5 | 0 | 770 | 0 | 0 | 7 | 770
43 | Sambalpur | B | Sambalpur | M. Corporation | 1 | Badsinghari road | 4 | Badsinghari school | 21.423637,83.935005 | Chaunpur road | 21.442809,83.951804 | 2900 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 145 | 145 | 0 | 0 | 0 | 145 | 6.525 | 2 | 3.2625 | 5 | 0 | 3190 | 0 | 0 | 29 | 3190
1 | Ganjam | A | Berhampur | M. Corporation | 10 | Aaina bandha | 3.5 | Pond Periphery | 19.309796,84.771092 | Not Applicable |  | 650 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole | Pond Periphery | 33 | 33 | 0 | 0 | 0 | 33 | 1.485 | 1 | 1.485 | 3 | 715 | 0 | 0 | 0 | 7 | 715
2 | Ganjam | A | Berhampur | M. Corporation | 14 | Salia bandha | 3.2 | Pond Periphery | 19.307920,84.775941 | Not Applicable |  | 440 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer | Pond Periphery | 22 | 22 | 0 | 0 | 0 | 22 | 0.99 | 1 | 0.99 | 3 | 484 | 0 | 0 | 0 | 4 | 484
3 | Ganjam | A | Berhampur | M. Corporation | 14 | Godi bandha | 3.5 | Pond Periphery | 19.301822,84.781579 | Not Applicable |  | 360 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole | Pond Periphery | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 396 | 0 | 0 | 0 | 4 | 396
4 | Ganjam | A | Berhampur | M. Corporation | 27 | Jagannath temple pond | 3.5 | Pond Periphery | 19.292376,84.792048 | Not Applicable |  | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole | Pond Periphery | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
6 | Ganjam | A | Berhampur | M. Corporation | 36-35 | Lanjipali nua bandha | 4 | Nua bandha pond peri periphery | 19.300245,84.808372 | Not Applicable |  | 900 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole | Pond Periphery | 45 | 45 | 0 | 0 | 0 | 45 | 2.025 | 1 | 2.025 | 3 | 990 | 0 | 0 | 0 | 9 | 990
7 | Ganjam | A | Berhampur | M. Corporation | 36 | Sanamudra pond | 3.4 | Pond Periphery | 19.293862,84.807461 | Not Applicable |  | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole | Pond Periphery | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
8 | Ganjam | A | Berhampur | M. Corporation | 37 | Singh bandha | 3.3 | Pond Periphery | 19.296774,84.815214 | Not Applicable |  | 2250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole | Pond Periphery | 113 | 113 | 0 | 0 | 0 | 113 | 5.085 | 2 | 2.5425 | 5 | 0 | 2475 | 0 | 0 | 23 | 2475
9 | Ganjam | A | Berhampur | M. Corporation | 38 | Botalu bandha | 4.5 | Pond Periphery | 19.297321,84.829015 | Not Applicable |  | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer | Pond Periphery | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
10 | Ganjam | A | Berhampur | M. Corporation | 38 | Jaleswar Khandi | 4 | Pond Periphery | 19.292839,84.830025 | Not Applicable |  | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer | Pond Periphery | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
12 | Ganjam | A | Berhampur | M. Corporation | 40 | Kalimandira temple | 4.5 | Pond Periphery | 19.316369,84.850513 | Not Applicable |  | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole | Pond Periphery | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
1 | Sundargarh | B | Rourkela | M. Corporation | 1 | Arnold road | 6 | Arnold School | 22.221539,84.785271 | Kalinga IDC | 22.222157,84.767164 | 1800 | M |  |  | Y |  | SS | 20 | 8 |  | Existing transformer |  | 90 | 90 | 0 | 0 | 90 | 0 | 6.3 | 1 | 6.3 | 12 | 0 | 0 | 0 | 1980 | 18 | 1980
2 | Sundargarh | B | Rourkela | M. Corporation | 1 | Jhadtarang village road | 3 | Pasatola chhack | 22.219350,84.782603 | Jhadtarang village | 22.213581,84.779902 | 550 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 605 | 0 | 0 | 0 | 6 | 605
3 | Sundargarh | B | Rourkela | M. Corporation | 1 | Jhadtarang market | 3 | Jhadtaranga market | 22.208580,84.776648 | Dandiapali | 22.210148,84.784458 | 1100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 55 | 55 | 0 | 0 | 0 | 55 | 2.475 | 1 | 2.475 | 5 | 0 | 1210 | 0 | 0 | 11 | 1210
4 | Sundargarh | B | Rourkela | M. Corporation | 1 | Dandiapali club to Paesatala | 3.5 | Dandiapali club | 22.215770,84.786224 | Parsatala chhack | 22.219191,84.782664 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
5 | Sundargarh | B | Rourkela | M. Corporation | 2 | Indoklory | 4 | Indoklory gate | 22.219767,84.765566 | Ending point | 22.220965,84.765618 | 100 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 5 | 5 | 0 | 0 | 0 | 5 | 0.225 | 1 | 0.225 | 3 | 110 | 0 | 0 | 0 | 1 | 110
6 | Sundargarh | B | Rourkela | M. Corporation | 2 | Bedbyash Collage road | 4 | Starting point | 22.237013,84.779028 | Ending point | 22.236463,84.786881 | 1750 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line |  | 88 | 88 | 0 | 0 | 0 | 88 | 3.96 | 1 | 3.96 | 5 | 0 | 1925 | 0 | 0 | 18 | 1925
7 | Sundargarh | B | Rourkela | M. Corporation | 3 | Munda basti | 7 | Starting point | 22.195303,84.841617 | Ending point | 22.193643,84.840832 | 450 | M |  |  | Y |  | SS | 27 | 9 |  | Existing street light pole |  | 17 | 17 | 0 | 0 | 17 | 0 | 1.19 | 1 | 1.19 | 3 | 495 | 0 | 0 | 0 | 3 | 495
8 | Sundargarh | B | Rourkela | M. Corporation | 24 | Bandamunda Khatal basti | 2 | Starting point | 22.230859,84.915836 | Ending point | 22.232339,84.915709 | 400 | M |  |  |  | Y | SS | 20 | 8 |  | Existing L.T line pole of Railway |  | 20 | 20 | 0 | 0 | 0 | 20 | 0.9 | 1 | 0.9 | 3 | 440 | 0 | 0 | 0 | 4 | 440
9 | Sundargarh | B | Rourkela | M. Corporation | 23 | Bangalipada | 2 | Starting point | 22.226525,84.909262 | Ending point | 22.225480,84.908968 | 130 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 7 | 7 | 0 | 0 | 0 | 7 | 0.315 | 1 | 0.315 | 3 | 143 | 0 | 0 | 0 | 1 | 143
10 | Sundargarh | B | Rourkela | M. Corporation | 37 | Jagda Mangala mandira chhack | 7 | Mangala mandira | 22.257391,84.905063 | Sadutal | 22.256345,84.908591 | 600 | M |  |  | Y |  | SS | 27 | 9 |  | Existing street light pole |  | 22 | 22 | 0 | 0 | 22 | 0 | 1.54 | 1 | 1.54 | 3 | 660 | 0 | 0 | 0 | 4 | 660
11 | Sundargarh | B | Rourkela | M. Corporation | 4 | Airport road | 5 | Starting point | 22.258050,84.806028 | Ending point | 22.258392,84.809629 | 1200 | M |  |  | Y |  | SS | 20 | 8 |  | Existing street light pole |  | 60 | 60 | 0 | 0 | 60 | 0 | 4.2 | 1 | 4.2 | 7.5 | 0 | 0 | 1320 | 0 | 12 | 1320
1 | Cuttack | A | Cuttack | Municipality | 56 | Bhutnath Temple To Bankei Thakurani Temple | 3.5 | Khathajodi River side | 20.439617,85.884962 | End Point | 20.440090,85.882632 | 750 | M |  |  |  | Y | SS | 20 | 8 |  | Existing transformer |  | 38 | 38 | 0 | 0 | 0 | 38 | 1.71 | 1 | 1.71 | 3 | 825 | 0 | 0 | 0 | 8 | 825
2 | Cuttack | A | Cuttack | Municipality | 56 | Keshab Swain Residence -Mukamaswar Hanuman Temple | 3.5 | Keshab Swain Residence | 20.444658,85.871334 | End Point | 20.446476,85.870242 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
3 | Cuttack | A | Cuttack | Municipality | 56 | Mukameswar Ganesh Mandap Ring Road | 3.5 | Start Point | 20.449246,85.866636 | Indira Colony | 20.445075,85.862444 | 750 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 38 | 38 | 0 | 0 | 0 | 38 | 1.71 | 1 | 1.71 | 3 | 825 | 0 | 0 | 0 | 8 | 825
4 | Cuttack | A | Cuttack | Municipality | 56 | Tentulinala Chhack__Cuttack-Banki Road | 3.5 | Start Point | 20.445371,85.864226 | Cuttack-Banki Main road | 20.440135,85.862311 | 850 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light pole |  | 43 | 43 | 0 | 0 | 0 | 43 | 1.935 | 1 | 1.935 | 3 | 935 | 0 | 0 | 0 | 9 | 935
5 | Cuttack | A | Cuttack | Municipality | 56 | Maa Duladei Tempule - Dr.PK Mishra Res. Via Uttampur Totasahi | 3.5 | Duladei Tempule | 20.438839,85.869804 | Dr.PK Mishra Res. Via Uttampur Totasahi | 20.437338,85.871379 | 650 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 33 | 33 | 0 | 0 | 0 | 33 | 1.485 | 1 | 1.485 | 3 | 715 | 0 | 0 | 0 | 7 | 715
6 | Cuttack | A | Cuttack | Municipality | 58 | Nuagarha Sani Temple Kenal Bridge | 3.5 | Start Point | 20.394374,85.877162 | Puruna sahi Nuagarha | 20.390791,85.881273 | 600 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 30 | 30 | 0 | 0 | 0 | 30 | 1.35 | 1 | 1.35 | 3 | 660 | 0 | 0 | 0 | 6 | 660
7 | Cuttack | A | Cuttack | Municipality | 58 | Purunasahi Beidge Hanuman Temple | 4 | Start Point | 20.387502,85.882758 | End Point | 20.385806,85.881722 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
8 | Cuttack | A | Cuttack | Municipality | 59 | Telenga Pentha-Nayahata gada | 3 | Telenga Pentha | 20.381414,85.889087 | Nayahata gada | 20.385636,85.888095 | 550 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 28 | 28 | 0 | 0 | 0 | 28 | 1.26 | 1 | 1.26 | 3 | 605 | 0 | 0 | 0 | 6 | 605
9 | Cuttack | A | Cuttack | Municipality | 59 | Kachera Kenal Bridge Road | 4 | Start Point | 20.364071,85.886013 | End Point | 20.360375,85.883977 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
10 | Cuttack | A | Cuttack | Municipality | 59 | Puruna Kachanala Bhoi sahi | 5 | Bhoi sahi Chhack | 20.361330,85.883228 | End Point |  | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
11 | Cuttack | A | Cuttack | Municipality | 59 | Trinatha Temple ring road | 3.5 | Trinatha Temple | 20.360235,85.880919 | End Point | 20.366166,85.886459 | 1000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 50 | 50 | 0 | 0 | 0 | 50 | 2.25 | 1 | 2.25 | 3 | 1100 | 0 | 0 | 0 | 10 | 1100
12 | Cuttack | A | Cuttack | Municipality | 59 | Lakheswar temple-Jogini Temple | 4 | Lakheswar temple back side | 20.358177,85.886516 | Jogini Temple | 20.375686,85.885696 | 2500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 125 | 125 | 0 | 0 | 0 | 125 | 5.625 | 2 | 2.8125 | 5 | 0 | 2750 | 0 | 0 | 25 | 2750
13 | Cuttack | A | Cuttack | Municipality | 58 | Jogini Temple -Juladei temple | 4 | Jogini Temple | 20.375686,85.885696 | Juladei temple | 20.388327,85.883294 | 1500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 75 | 75 | 0 | 0 | 0 | 75 | 3.375 | 1 | 3.375 | 5 | 0 | 1650 | 0 | 0 | 15 | 1650
14 | Cuttack | A | Cuttack | Municipality | 49 | Kendrapada kenal side road | 4 | Sai international school | 20.504734,85.928093 | End Point | 20.503169,85.930947 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
15 | Cuttack | A | Cuttack | Municipality | 49 | Kendrapada sub-kenal side road | 3.5 | Start Point | 20.508113,85.937587 | End Point | 20.505821,85.926093 | 1500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 75 | 75 | 0 | 0 | 0 | 75 | 3.375 | 1 | 3.375 | 5 | 0 | 1650 | 0 | 0 | 15 | 1650
16 | Cuttack | A | Cuttack | Municipality | 49 | Nua sahi village road | 4 | Start Point | 20.508965,85.944186 | End Point | 20.509277,85.937645 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
17 | Cuttack | A | Cuttack | Municipality | 49 | Andhari village- Birupakheswar temple | 4 | Start Point | 20.511110,85.931224 | End Point | 20.510959,85.927871 | 350 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole | Realway over bridge | 18 | 18 | 0 | 0 | 0 | 18 | 0.81 | 1 | 0.81 | 3 | 385 | 0 | 0 | 0 | 4 | 385
18 | Cuttack | A | Cuttack | Municipality | 48 | Kendrapada kenal side road | 4 | Start Point | 20.507315,85.919428 | Laxmanpur | 20.509970,85.817716 | 700 | M |  |  |  | Y | SS | 20 | 8 |  | Existing LT pole |  | 35 | 35 | 0 | 0 | 0 | 35 | 1.575 | 1 | 1.575 | 3 | 770 | 0 | 0 | 0 | 7 | 770
19 | Cuttack | A | Cuttack | Municipality | 48/49 | Andhari village- kenal road | 3.5 | Bishnu Mallick | 20.508024,85.926441 | End Point | 20.507673,85.924023 | 250 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light | Realway over bridge | 13 | 13 | 0 | 0 | 0 | 13 | 0.585 | 1 | 0.585 | 3 | 275 | 0 | 0 | 0 | 3 | 275
20 | Cuttack | A | Cuttack | Municipality | 49 | L .N .C Collage- Torol road | 3.5 | L .N .C Collage | 20.497158,85.926968 | Torol road | 20.496732,85.927315 | 200 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 10 | 10 | 0 | 0 | 0 | 10 | 0.45 | 1 | 0.45 | 3 | 220 | 0 | 0 | 0 | 2 | 220
21 | Cuttack | A | Cuttack | Municipality | 49 | Basti road(Near Khadai Hotel ) | 3.5 | Rajan Lenka house | 20.493489,85.932547 | End Point | 20.493575,85.931463 | 150 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 8 | 8 | 0 | 0 | 0 | 8 | 0.36 | 1 | 0.36 | 3 | 165 | 0 | 0 | 0 | 2 | 165
22 | Cuttack | A | Cuttack | Municipality | 55 | Mahanadi Ring Road(Gandhipalli) | 4 | Kanheipur(Gandhipalli) | 20.458081,85.925353 | End Point | 20.447003,85.944114 | 3000 | M |  |  |  | Y | SS | 20 | 8 |  | Existing Transformer |  | 150 | 150 | 0 | 0 | 0 | 150 | 6.75 | 2 | 3.375 | 5 | 0 | 3300 | 0 | 0 | 30 | 3300
23 | Cuttack | A | Cuttack | Municipality | 55 | Raghunath Vihar-Bidyadharpur(Bhoi sahi) | 4 | Raghunath Vihar | 20.455753,85.926100 | Bidyadharpur(Bhoi sahi) | 20.454742,85.925342 | 500 | M |  |  |  | Y | SS | 20 | 8 |  | Existing street light |  | 25 | 25 | 0 | 0 | 0 | 25 | 1.125 | 1 | 1.125 | 3 | 550 | 0 | 0 | 0 | 5 | 550
Note on N3: Author: One Way, Two Way
Note on S3: More, Chandrarao (IN - Mumbai): (single sided, double sided, median, Zig -Zag etc. )
Note on T3: More, Chandrarao (IN - Mumbai): Dist. between two adjacent poles with respect to next pole - on same side of road
Note on U3: Author: For Given pole arrangement what should be height of pole
Note on V3: More, Chandrarao (IN - Mumbai): For Site Specific Situation - say adjucent servixce road of lower width
Note on S5: More, Chandrarao (IN - Mumbai): Middle pole arrangement not recommended as it would create hurdle for Marine Movement
Note on S71: More, Chandrarao (IN - Mumbai): Due to Higher Divider Width - Both Side Pole Arrangement Proposed